CABLE & WIRE FOR ELECTRICAL, ELV AND INDUSTRIAL PROJECTS

# 600/1000 V ABC Aerial Bundled Cable NFC 33-209

Exact model: ABC NFC 33-209

PRODUCT IMAGES

ABC NFC 33-209 · Primary

PRODUCT OVERVIEW

NexPro 600/1000 V ABC Aerial Bundled Cable NFC 33-209 is supplied as a configurable aerial bundled cable product family. Catalog models are preserved exactly as ABC NFC 33-209. Use the source-derived tables below to select the required conductor construction, core arrangement, cross-section and dimensions.

| Product line | Cable & Wire for Electrical, ELV and Industrial Projects |
| --- | --- |
| Series / family | Aerial bundled cable |
| Exact model | ABC NFC 33-209 |
| Applications | Solar and utility projects, Outdoor distribution, Project-specific installations |

MODEL IDENTIFICATION

| Exact model | Product / variant | Cable category | Catalog model | Configuration |
| --- | --- | --- | --- | --- |
| ABC NFC 33-209 | 600/1000 V ABC Aerial Bundled Cable NFC 33-209 | Aerial bundled cable | ABC NFC 33-209 | Select from source table |

TECHNICAL SPECIFICATIONS

| Parameter | Specification |
| --- | --- |
| Cable category | Aerial bundled cable |
| Catalog model | ABC NFC 33-209 |
| Configuration | Select from source table |
| Manufacturer models | ABC NFC 33-209 |
| mm^2 | max. conductor-resistance: Ohm/km ¦ min. breaking load of conductor strand: kN ¦ Current rating in the air: A ¦ Outer diameter: mm ¦ Total weight: kg/km |
| 2x10 RM | max. conductor-resistance: 3.080 ¦ min. breaking load of conductor strand: 1.5 ¦ Current rating in the air: 38 ¦ Outer diameter: 12.8 ¦ Total weight: 93 |
| 4x10 RM | max. conductor-resistance: 3.080 ¦ min. breaking load of conductor strand: 1.5 ¦ Current rating in the air: 38 ¦ Outer diameter: 15.4 ¦ Total weight: 183 |
| 2x16 RM | max. conductor-resistance: 1.910 ¦ min. breaking load of conductor strand: 2.3 ¦ Current rating in the air: 72 ¦ Outer diameter: 14.8 ¦ Total weight: 129 |
| 2x16 RN + 2x1.5 RE | max. conductor-resistance: 1.910/12.100 ¦ min. breaking load of conductor strand: 2.3 ¦ Current rating in the air: 72 ¦ Outer diameter: 14.8 ¦ Total weight: 176 |
| 4x16 RM | max. conductor-resistance: 1.910 ¦ min. breaking load of conductor strand: 2.3 ¦ Current rating in the air: 72 ¦ Outer diameter: 17.8 ¦ Total weight: 257 |
| 4x16 RN + 2x1.5 RE | max. conductor-resistance: 1.910/12.100 ¦ min. breaking load of conductor strand: 2.3 ¦ Current rating in the air: 72 ¦ Outer diameter: 17.8 ¦ Total weight: 304 |
| 2x25 RM | max. conductor-resistance: 1.200 ¦ min. breaking load of conductor strand: 3.8 ¦ Current rating in the air: 107 ¦ Outer diameter: 18.0 ¦ Total weight: 202 |

ENGINEERING TABLES

ABC NFC 33-209 · Source Specification Table 1

| Number of cores x nominal cross section | max. conductor-resistance | min. breaking load of conductor strand | Current rating in the air | Outer diameter | Total weight |
| --- | --- | --- | --- | --- | --- |
| mm^2 | Ohm/km | kN | A | mm | kg/km |
| 2x10 RM | 3.080 | 1.5 | 38 | 12.8 | 93 |
| 4x10 RM | 3.080 | 1.5 | 38 | 15.4 | 183 |
| 2x16 RM | 1.910 | 2.3 | 72 | 14.8 | 129 |
| 2x16 RN + 2x1.5 RE | 1.910/12.100 | 2.3 | 72 | 14.8 | 176 |
| 4x16 RM | 1.910 | 2.3 | 72 | 17.8 | 257 |
| 4x16 RN + 2x1.5 RE | 1.910/12.100 | 2.3 | 72 | 17.8 | 304 |
| 2x25 RM | 1.200 | 3.8 | 107 | 18.0 | 202 |
| 2x25 RM + 2x1,5 RE | 1.200/12.100 | 3.8 | 107 | 18.0 | 249 |
| 4x25 RM | 1.200 | 3.8 | 107 | 21.7 | 404 |
| 4x25 RM + 2x1,5 RE | 1.200/12.100 | 3.8 | 107 | 21.7 | 451 |
| 2x35 RM | 0.868 | 5.2 | 132 | 20.8 | 269 |
| 2x35 RM + 2x1,5 RE | 0.868/12.100 | 5.2 | 132 | 20.8 | 316 |
| 4x35 RM | 0.868 | 5.2 | 132 | 25.1 | 539 |
| 4x35 RM + 2x1,5 RE | 0.868/12.100 | 5.2 | 132 | 25.1 | 586 |
| 2x50 RM | 0.641 | 7.6 | 165 | 23.4 | 352 |
| 2x35 RM + 2x1,5 RE | 0.868/12.100 | 5.2 | 132 | 20.8 | 316 |
| 4x35 RM | 0.868 | 5.2 | 132 | 25.1 | 539 |
| 4x35 RM + 2x1,5 RE | 0.868/12.100 | 5.2 | 132 | 25.1 | 586 |
| 2x50 RM | 0.641 | 7.6 | 165 | 23.4 | 352 |
| 2x50 RM + 2x1,5 RE | 0.641/12.100 | 7.6 | 165 | 23.4 | 399 |
| 1x54.6 RM + 3x25 RM | 0.630/1.200 | 3.8 | 107 | 21.7 | 507 |
| 1x54.6 RM + 3x25 RM + 1x16 RM | 0.630/1.200/1.910 | 3.8/2.3 | 107/72 | 24.3 | 573 |
| 1x54.6 RM + 3x25 RM + 2x16 RM | 0.630/1.200/1.910 | 3.8/2.3 | 107/72 | 29.7 | 639 |
| 1x54.6 RM + 3x25 RM + 3x16 RM | 0.630/1.200/1.910 | 3.8/2.3 | 107/72 | 31.1 | 705 |
| 1x54.6 RM + 3x35 RM | 0.630/0.868 | 5.2 | 132 | 25.1 | 615 |
| 1x54.6 RM + 3x35 RM + 1x16 RM | 0.630/0.868/1.910 | 5.2/2.3 | 132/72 | 28.1 | 680 |
| 1x54.6 RM + 3x35 RM + 2x16 RM | 0.630/0.868/1.910 | 5.2/2.3 | 132/72 | 34.3 | 748 |
| 1x54.6 RM + 3x35 RM + 3x16 RM | 0.630/0.868/1.910 | 5.2/2.3 | 132/72 | 35.9 | 814 |
| 1x54.6 RM + 3x35 RM + 1x25 RM | 0.630/0.868/1.200 | 5.2/3.8 | 132/107 | 28.1 | 714 |
| 1x54.6 RM + 3x50 RM | 0.630/0.641 | 7.6 | 165 | 28.2 | 741 |
| 1x54.6 RM + 3x50 RM + 1x16 RM | 0.630/0.641/1.910 | 7.6/2.3 | 165/72 | 31.6 | 806 |
| 1x54.6 RM + 3x50 RM + 2x16 RM | 0.630/0.641/1.910 | 7.6/2.3 | 165/72 | 38.6 | 875 |
| 1x54.6 RM + 3x50 RM + 3x16 RM | 0.630/0.641/1.910 | 7.6/2.3 | 165/72 | 40.4 | 940 |
| 1x54.6 RM + 3x50 RM + 1x25 RM | 0.630/0.641/1.200 | 7.6/3.8 | 165/107 | 31.6 | 841 |
| 1x54.6 RM + 3x70 RM | 0.630/0.443 | 10.2 | 205 | 33.0 | 950 |
| 1x54.6 RM + 3x70 RM + 1x16 RM | 0.630/0.443/1.910 | 10.2/2.3 | 205/72 | 37.0 | 1014 |
| 1x54.6 RM + 3x70 RM + 2x16 RM | 0.630/0.443/1.910 | 10.2/2.3 | 205/72 | 45.2 | 1083 |
| 1x54.6 RM + 3x70 RM + 3x16 RM | 0.630/0.443/1.910 | 10.2/2.3 | 205/72 | 47.3 | 1148 |
| 1x54.6 RM + 3x70 RM + 1x25 RM | 0.630/0.443/1.200 | 10.2/3.8 | 205/107 | 37.0 | 1048 |
| 1x54.6 RM + 3x70 RM + 2x25 RM | 0.630/0.443/1.200 | 10.2/3.8 | 205/107 | 45.2 | 1150 |
| 1x54.6 RM + 3x70 RM + 3x25 RM | 0.630/0.443/1.200 | 10.2/3.8 | 205/107 | 47.3 | 1250 |
| 1x54.6 RM + 3x95 RM | 0.630/0.320 | 13.5 | 240 | 37.4 | 1176 |
| 1x54.6 RM + 3x95 RM + 1x16 RM | 0.630/0.320/1.910 | 13.5/2.3 | 240/72 | 41.9 | 1243 |