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	PRODUCT SPECIFICATION
Aerial bundled cable
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CABLE & WIRE FOR ELECTRICAL, ELV AND INDUSTRIAL PROJECTS
600/1000 V ABC Aerial Bundled Cable NFC 33-209
Exact model: ABC NFC 33-209
PRODUCT IMAGES
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	ABC NFC 33-209 · Primary



PRODUCT OVERVIEW
NexPro 600/1000 V ABC Aerial Bundled Cable NFC 33-209 is supplied as a configurable aerial bundled cable product family. Catalog models are preserved exactly as ABC NFC 33-209. Use the source-derived tables below to select the required conductor construction, core arrangement, cross-section and dimensions.
	Product line
	Cable & Wire for Electrical, ELV and Industrial Projects

	Series / family
	Aerial bundled cable

	Exact model
	ABC NFC 33-209

	Applications
	Solar and utility projects, Outdoor distribution, Project-specific installations


MODEL IDENTIFICATION
	Exact model
	Product / variant
	Cable category
	Catalog model
	Configuration

	ABC NFC 33-209
	600/1000 V ABC Aerial Bundled Cable NFC 33-209
	Aerial bundled cable
	ABC NFC 33-209
	Select from source table


TECHNICAL SPECIFICATIONS
	Parameter
	Specification

	Cable category
	Aerial bundled cable

	Catalog model
	ABC NFC 33-209

	Configuration
	Select from source table

	Manufacturer models
	ABC NFC 33-209

	mm^2
	max. conductor-resistance: Ohm/km | min. breaking load of conductor strand: kN | Current rating in the air: A | Outer diameter: mm | Total weight: kg/km

	2x10 RM
	max. conductor-resistance: 3.080 | min. breaking load of conductor strand: 1.5 | Current rating in the air: 38 | Outer diameter: 12.8 | Total weight: 93

	4x10 RM
	max. conductor-resistance: 3.080 | min. breaking load of conductor strand: 1.5 | Current rating in the air: 38 | Outer diameter: 15.4 | Total weight: 183

	2x16 RM
	max. conductor-resistance: 1.910 | min. breaking load of conductor strand: 2.3 | Current rating in the air: 72 | Outer diameter: 14.8 | Total weight: 129

	2x16 RN + 2x1.5 RE
	max. conductor-resistance: 1.910/12.100 | min. breaking load of conductor strand: 2.3 | Current rating in the air: 72 | Outer diameter: 14.8 | Total weight: 176

	4x16 RM
	max. conductor-resistance: 1.910 | min. breaking load of conductor strand: 2.3 | Current rating in the air: 72 | Outer diameter: 17.8 | Total weight: 257

	4x16 RN + 2x1.5 RE
	max. conductor-resistance: 1.910/12.100 | min. breaking load of conductor strand: 2.3 | Current rating in the air: 72 | Outer diameter: 17.8 | Total weight: 304

	2x25 RM
	max. conductor-resistance: 1.200 | min. breaking load of conductor strand: 3.8 | Current rating in the air: 107 | Outer diameter: 18.0 | Total weight: 202


ENGINEERING TABLES
ABC NFC 33-209 · Source Specification Table 1
	Number of cores x nominal cross section
	max. conductor-resistance
	min. breaking load of conductor strand
	Current rating in the air
	Outer diameter
	Total weight

	mm^2
	Ohm/km
	kN
	A
	mm
	kg/km

	2x10 RM
	3.080
	1.5
	38
	12.8
	93

	4x10 RM
	3.080
	1.5
	38
	15.4
	183

	2x16 RM
	1.910
	2.3
	72
	14.8
	129

	2x16 RN + 2x1.5 RE
	1.910/12.100
	2.3
	72
	14.8
	176

	4x16 RM
	1.910
	2.3
	72
	17.8
	257

	4x16 RN + 2x1.5 RE
	1.910/12.100
	2.3
	72
	17.8
	304

	2x25 RM
	1.200
	3.8
	107
	18.0
	202

	2x25 RM + 2x1,5 RE
	1.200/12.100
	3.8
	107
	18.0
	249

	4x25 RM
	1.200
	3.8
	107
	21.7
	404

	4x25 RM + 2x1,5 RE
	1.200/12.100
	3.8
	107
	21.7
	451

	2x35 RM
	0.868
	5.2
	132
	20.8
	269

	2x35 RM + 2x1,5 RE
	0.868/12.100
	5.2
	132
	20.8
	316

	4x35 RM
	0.868
	5.2
	132
	25.1
	539

	4x35 RM + 2x1,5 RE
	0.868/12.100
	5.2
	132
	25.1
	586

	2x50 RM
	0.641
	7.6
	165
	23.4
	352

	2x35 RM + 2x1,5 RE
	0.868/12.100
	5.2
	132
	20.8
	316

	4x35 RM
	0.868
	5.2
	132
	25.1
	539

	4x35 RM + 2x1,5 RE
	0.868/12.100
	5.2
	132
	25.1
	586

	2x50 RM
	0.641
	7.6
	165
	23.4
	352

	2x50 RM + 2x1,5 RE
	0.641/12.100
	7.6
	165
	23.4
	399

	1x54.6 RM + 3x25 RM
	0.630/1.200
	3.8
	107
	21.7
	507

	1x54.6 RM + 3x25 RM + 1x16 RM
	0.630/1.200/1.910
	3.8/2.3
	107/72
	24.3
	573

	1x54.6 RM + 3x25 RM + 2x16 RM
	0.630/1.200/1.910
	3.8/2.3
	107/72
	29.7
	639

	1x54.6 RM + 3x25 RM + 3x16 RM
	0.630/1.200/1.910
	3.8/2.3
	107/72
	31.1
	705

	1x54.6 RM + 3x35 RM
	0.630/0.868
	5.2
	132
	25.1
	615

	1x54.6 RM + 3x35 RM + 1x16 RM
	0.630/0.868/1.910
	5.2/2.3
	132/72
	28.1
	680

	1x54.6 RM + 3x35 RM + 2x16 RM
	0.630/0.868/1.910
	5.2/2.3
	132/72
	34.3
	748

	1x54.6 RM + 3x35 RM + 3x16 RM
	0.630/0.868/1.910
	5.2/2.3
	132/72
	35.9
	814

	1x54.6 RM + 3x35 RM + 1x25 RM
	0.630/0.868/1.200
	5.2/3.8
	132/107
	28.1
	714

	1x54.6 RM + 3x50 RM
	0.630/0.641
	7.6
	165
	28.2
	741

	1x54.6 RM + 3x50 RM + 1x16 RM
	0.630/0.641/1.910
	7.6/2.3
	165/72
	31.6
	806

	1x54.6 RM + 3x50 RM + 2x16 RM
	0.630/0.641/1.910
	7.6/2.3
	165/72
	38.6
	875

	1x54.6 RM + 3x50 RM + 3x16 RM
	0.630/0.641/1.910
	7.6/2.3
	165/72
	40.4
	940

	1x54.6 RM + 3x50 RM + 1x25 RM
	0.630/0.641/1.200
	7.6/3.8
	165/107
	31.6
	841

	1x54.6 RM + 3x70 RM
	0.630/0.443
	10.2
	205
	33.0
	950

	1x54.6 RM + 3x70 RM + 1x16 RM
	0.630/0.443/1.910
	10.2/2.3
	205/72
	37.0
	1014

	1x54.6 RM + 3x70 RM + 2x16 RM
	0.630/0.443/1.910
	10.2/2.3
	205/72
	45.2
	1083

	1x54.6 RM + 3x70 RM + 3x16 RM
	0.630/0.443/1.910
	10.2/2.3
	205/72
	47.3
	1148

	1x54.6 RM + 3x70 RM + 1x25 RM
	0.630/0.443/1.200
	10.2/3.8
	205/107
	37.0
	1048

	1x54.6 RM + 3x70 RM + 2x25 RM
	0.630/0.443/1.200
	10.2/3.8
	205/107
	45.2
	1150

	1x54.6 RM + 3x70 RM + 3x25 RM
	0.630/0.443/1.200
	10.2/3.8
	205/107
	47.3
	1250

	1x54.6 RM + 3x95 RM
	0.630/0.320
	13.5
	240
	37.4
	1176

	1x54.6 RM + 3x95 RM + 1x16 RM
	0.630/0.320/1.910
	13.5/2.3
	240/72
	41.9
	1243
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