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CABLE & WIRE FOR ELECTRICAL, ELV AND INDUSTRIAL PROJECTS
H05V-K Flexible PVC Insulated Wire
Exact model: H05V-K
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PRODUCT OVERVIEW
NexPro H05V-K Flexible PVC Insulated Wire is supplied as a configurable single-core flexible wire product family. Catalog models are preserved exactly as H05V-K. Use the source-derived tables below to select the required conductor construction, core arrangement, cross-section and dimensions.
	Product line
	Cable & Wire for Electrical, ELV and Industrial Projects

	Series / family
	Single-core flexible wire

	Exact model
	H05V-K

	Applications
	Equipment connections, Flexible wiring, OEM electrical assemblies


MODEL IDENTIFICATION
	Exact model
	Product / variant
	Cable category
	Catalog model
	Configuration

	H05V-K
	H05V-K Flexible PVC Insulated Wire
	Single-core flexible wire
	H05V-K
	Select from source table


TECHNICAL SPECIFICATIONS
	Parameter
	Specification

	Cable category
	Single-core flexible wire

	Catalog model
	H05V-K

	Configuration
	Select from source table

	Manufacturer models
	H05V-K

	1x0,5
	Resistance at 20 °C
(Ohm/km): 39 | External Diameter (mm): 2,15 | Weight (kg/km): 9 | Class: Eca

	1x0,75
	Resistance at 20 °C
(Ohm/km): 26 | External Diameter (mm): 2,25 | Weight (kg/km): 11 | Class: Eca

	1x1
	Resistance at 20 °C
(Ohm/km): 19,5 | External Diameter (mm): 2,50 | Weight (kg/km): 14 | Class: Eca


ENGINEERING TABLES
H05V-K · Source Specification Table 1
	Section (mm²)
	Resistance at 20 °C (Ohm/km)
	External Diameter (mm)
	Weight (kg/km)
	Class

	1x0,5
	39
	2,15
	9
	Eca

	1x0,75
	26
	2,25
	11
	Eca

	1x1
	19,5
	2,50
	14
	Eca


H05V-K · Source Specification Table 2
	1. Conductor
	Flexible electrolytic copper conductor (Class V) according to BS EN 60228:2005 (previously BS6360) and EN 60228.

	2. Insulation
	PVC insulation type TI-1 according to BS7655 and HD 21.3S3:1995/A2:2008.

	Nominal voltage
	300/500 V

	Test voltage
	2.000 V A.C.

	Maximum temperature
	70 °C

	Other characteristics
	—

	Colours according to HD 21.1S4:2002Non-flame propagating according to UNE-EN 60332-1-2, EN 60332-1-2 and IEC 60332-1-2CPR Classification according to EN 50575
	—
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