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	PRODUCT SPECIFICATION
Single-core building wire
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CABLE & WIRE FOR ELECTRICAL, ELV AND INDUSTRIAL PROJECTS
H05V-U / H07V-U PVC Insulated Solid Building Wire
Exact model: H05V-U | H07V-U
PRODUCT IMAGES
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	H05V-U | H07V-U · Primary



PRODUCT OVERVIEW
NexPro H05V-U / H07V-U PVC Insulated Solid Building Wire is supplied as a configurable single-core building wire product family. Catalog models are preserved exactly as H05V-U, H07V-U. Use the source-derived tables below to select the required conductor construction, core arrangement, cross-section and dimensions.
	Product line
	Cable & Wire for Electrical, ELV and Industrial Projects

	Series / family
	Single-core building wire

	Exact model
	H05V-U | H07V-U

	Applications
	Building wiring, Electrical panels, Fixed installation projects


MODEL IDENTIFICATION
	Exact model
	Product / variant
	Cable category
	Catalog model
	Configuration

	H05V-U | H07V-U
	H05V-U / H07V-U PVC Insulated Solid Building Wire
	Single-core building wire
	H05V-U | H07V-U
	Select from source table


TECHNICAL SPECIFICATIONS
	Parameter
	Specification

	Cable category
	Single-core building wire

	Catalog model
	H05V-U | H07V-U

	Configuration
	Select from source table

	Manufacturer models
	H05V-U / H07V-U

	Conductor
	Specified value: Bare solid copper

	Insulation
	Specified value: PVC

	Minimum bending radius, fixed installation
	Specified value: 4xOD

	Colour
	Specified value: According to EN 50525-1


ENGINEERING TABLES
H05V-U | H07V-U · Construction
	Parameter
	Specified value

	Conductor
	Bare solid copper

	Insulation
	PVC

	Minimum bending radius, fixed installation
	4xOD

	Colour
	According to EN 50525-1


H05V-U | H07V-U · Source Specification Table 2
	Type Code
	Cross-section [mm]
	Nominal Outer Diameter [mm]
	Current rating, installation in open air, ambient 30°C [A]
	Total weight [kg/km]

	H05V-U
	0,5
	2,0
	12
	9

	H05V-U
	0,75
	2,2
	15
	11

	H05V-U
	1
	2,3
	19
	14

	H07V-U
	1,5
	2,8
	24
	20

	H07V-U
	2,5
	3,4
	32
	31

	H07V-U
	4
	3,8
	42
	46

	H07V-U
	6
	4,3
	54
	68

	H07V-U
	10
	5,4
	73
	111
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