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CABLE & WIRE FOR ELECTRICAL, ELV AND INDUSTRIAL PROJECTS
H07V-K Flexible PVC Insulated Wire
Exact model: H07V-K
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PRODUCT OVERVIEW
NexPro H07V-K Flexible PVC Insulated Wire is supplied as a configurable single-core flexible wire product family. Catalog models are preserved exactly as H07V-K. Use the source-derived tables below to select the required conductor construction, core arrangement, cross-section and dimensions.
	Product line
	Cable & Wire for Electrical, ELV and Industrial Projects

	Series / family
	Single-core flexible wire

	Exact model
	H07V-K

	Applications
	Equipment connections, Flexible wiring, OEM electrical assemblies


MODEL IDENTIFICATION
	Exact model
	Product / variant
	Cable category
	Catalog model
	Configuration

	H07V-K
	H07V-K Flexible PVC Insulated Wire
	Single-core flexible wire
	H07V-K
	Select from source table


TECHNICAL SPECIFICATIONS
	Parameter
	Specification

	Cable category
	Single-core flexible wire

	Catalog model
	H07V-K

	Configuration
	Select from source table

	Manufacturer models
	H07V-K

	1.5
	Conductor diam.
(mm): 1.55 | Nom. o u t e r d i a m . (mm): 3.50 | Permissible current rating (3 conductors) (A): 15.5 | Permissible current (One phase) (A): 17.5 | Approx. weight (kg/km): 21

	2.5
	Conductor diam.
(mm): 2.00 | Nom. o u t e r d i a m . (mm): 4.2 | Permissible current rating (3 conductors) (A): 21.0 | Permissible current (One phase) (A): 24.0 | Approx. weight (kg/km): 35

	4
	Conductor diam.
(mm): 2.50 | Nom. o u t e r d i a m . (mm): 4.8 | Permissible current rating (3 conductors) (A): 28.0 | Permissible current (One phase) (A): 32.0 | Approx. weight (kg/km): 45

	6
	Conductor diam.
(mm): 3.00 | Nom. o u t e r d i a m . (mm): 6.3 | Permissible current rating (3 conductors) (A): 36.0 | Permissible current (One phase) (A): 41.0 | Approx. weight (kg/km): 68

	10
	Conductor diam.
(mm): 4.00 | Nom. o u t e r d i a m . (mm): 7.6 | Permissible current rating (3 conductors) (A): 50.0 | Permissible current (One phase) (A): 57.0 | Approx. weight (kg/km): 115

	16
	Conductor diam.
(mm): 5.45 | Nom. o u t e r d i a m . (mm): 8.8 | Permissible current rating (3 conductors) (A): 68.0 | Permissible current (One phase) (A): 76.0 | Approx. weight (kg/km): 183

	25
	Conductor diam.
(mm): 6.60 | Nom. o u t e r d i a m . (mm): 11.0 | Permissible current rating (3 conductors) (A): 89.0 | Permissible current (One phase) (A): 96.0 | Approx. weight (kg/km): 290

	35
	Conductor diam.
(mm): 8.00 | Nom. o u t e r d i a m . (mm): 12.5 | Permissible current rating (3 conductors) (A): 110.0 | Permissible current (One phase) (A): 119.0 | Approx. weight (kg/km): 320


ENGINEERING TABLES
H07V-K · Source Specification Table 1
	Cross section (mm²)
	Conductor diam. (mm)
	Nom. o u t e r d i a m . (mm)
	Permissible current rating (3 conductors) (A)
	Permissible current (One phase) (A)
	Approx. weight (kg/km)

	1.5
	1.55
	3.50
	15.5
	17.5
	21

	2.5
	2.00
	4.2
	21.0
	24.0
	35

	4
	2.50
	4.8
	28.0
	32.0
	45

	6
	3.00
	6.3
	36.0
	41.0
	68

	10
	4.00
	7.6
	50.0
	57.0
	115

	16
	5.45
	8.8
	68.0
	76.0
	183

	25
	6.60
	11.0
	89.0
	96.0
	290

	35
	8.00
	12.5
	110.0
	119.0
	320

	50
	9.50
	14.5
	134.0
	144.0
	470

	70
	11.30
	17.0
	171.0
	184.0
	505

	95
	13.60
	19.0
	207.0
	223.0
	756

	120
	15.20
	21.0
	239.0
	259.0
	1120

	150
	16.70
	23.5
	275.0
	299.0
	1525

	185
	18.80
	26.0
	315.0
	341.0
	1890

	240
	21.20
	29.5
	371.0
	403.0
	2340
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