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	PRODUCT SPECIFICATION
Halogen-free installation cable
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CABLE & WIRE FOR ELECTRICAL, ELV AND INDUSTRIAL PROJECTS
NHXMH Halogen-Free Sheathed Installation Cable
Exact model: NHXMH
PRODUCT IMAGES
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	NHXMH · Primary



PRODUCT OVERVIEW
NexPro NHXMH Halogen-Free Sheathed Installation Cable is supplied as a configurable halogen-free installation cable product family. Catalog models are preserved exactly as NHXMH. Use the source-derived tables below to select the required conductor construction, core arrangement, cross-section and dimensions.
	Product line
	Cable & Wire for Electrical, ELV and Industrial Projects

	Series / family
	Halogen-free installation cable

	Exact model
	NHXMH

	Applications
	Public buildings, Emergency circuits, Low-smoke installation projects


MODEL IDENTIFICATION
	Exact model
	Product / variant
	Cable category
	Catalog model
	Configuration

	NHXMH
	NHXMH Halogen-Free Sheathed Installation Cable
	Halogen-free installation cable
	NHXMH
	Select from source table


TECHNICAL SPECIFICATIONS
	Parameter
	Specification

	Cable category
	Halogen-free installation cable

	Catalog model
	NHXMH

	Configuration
	Select from source table

	Manufacturer models
	NHXMH

	Test voltage
	Column 2:  | [V]: [V]_{AC} | 300 / 500 Volt: 2000 | Column 5:

	Temperature range
	Column 2: in motion | [V]:  | 300 / 500 Volt: -5°C till +70°C | Column 5:

	Operating temperature
	Column 2: short circuit | [V]: °C | 300 / 500 Volt: 160 | Column 5:

	Short circuit time
	Column 2: max. | [V]: [sec] | 300 / 500 Volt: 5 | Column 5:

	Bending radius
	Column 2: in motion | [V]: x diameter | 300 / 500 Volt: 12 | Column 5:

	Flammability
	Column 2: standard | [V]:  | 300 / 500 Volt: EN 50266-2-4 | Column 5:

	Source parameter
	Column 2:  | [V]:  | 300 / 500 Volt: EN 60332-1 | Column 5:; Column 2:  | [V]:  | 300 / 500 Volt: IEC 60332-3 Kat.C | Column 5:


ENGINEERING TABLES
NHXMH · Source Specification Table 1
	Nominal voltage Uo/U
	Column 2
	[V]
	300 / 500 Volt
	Column 5

	Test voltage
	Not provided
	[V]_{AC}
	2000
	Not provided

	Temperature range
	in motion
	Not provided
	-5°C till +70°C
	Not provided

	Operating temperature
	short circuit
	°C
	160
	Not provided

	Short circuit time
	max.
	[sec]
	5
	Not provided

	Bending radius
	in motion
	x diameter
	12
	Not provided

	Flammability
	standard
	Not provided
	EN 50266-2-4
	Not provided

	Not provided
	Not provided
	Not provided
	EN 60332-1
	Not provided

	Not provided
	Not provided
	Not provided
	IEC 60332-3 Kat.C
	Not provided

	Number of cores and nominal cross section mm^2
	Not provided
	Copper figurekg/km
	Cond. construction (appr. value)mm
	Overall diameter appr. mm

	2 x 1,5
	Not provided
	30
	1 x 1,38
	8,7

	2 x 2,5
	Not provided
	50
	1 x 1,38
	9,5

	3 x 1,5
	Not provided
	45
	1 x 1,38
	9,1

	3 x 2,5
	Not provided
	75
	1 x 1,78
	9,9

	3 x 4
	Not provided
	120
	1 x 2,25
	11,2

	3 x 6
	Not provided
	180
	1 x 2,76
	12,7

	3 x 10
	Not provided
	300
	1 x 3,56
	15,3

	4 x 1,5
	Not provided
	60
	1 x 1,38
	9,7

	4 x 2,5
	Not provided
	100
	1 x 1,78
	10,6

	4 x 4
	Not provided
	160
	1 x 2,25
	12,5

	4 x 6
	Not provided
	240
	1 x 2,76
	13,7

	4 x 10
	Not provided
	400
	1 x 3,56
	16,5

	4 x 16 RM
	Not provided
	640
	7 x 1,70
	19,4

	5 x 1,5
	Not provided
	75
	1 x 1,38
	10,4

	5 x 2,5
	Not provided
	125
	1 x 1,78
	11,5

	5 x 4
	Not provided
	200
	1 x 2,25
	13,5

	5 x 6
	Not provided
	300
	1 x 2,76
	15,3



	NexPro Product Intelligence
	Confirm final configuration in the project RFQ
	Page 1


image2.png




image3.jpg




image1.png








