CABLE & WIRE FOR ELECTRICAL, ELV AND INDUSTRIAL PROJECTS

# NHXMH Halogen-Free Sheathed Installation Cable

Exact model: NHXMH

PRODUCT IMAGES

NHXMH · Primary

PRODUCT OVERVIEW

NexPro NHXMH Halogen-Free Sheathed Installation Cable is supplied as a configurable halogen-free installation cable product family. Catalog models are preserved exactly as NHXMH. Use the source-derived tables below to select the required conductor construction, core arrangement, cross-section and dimensions.

| Product line | Cable & Wire for Electrical, ELV and Industrial Projects |
| --- | --- |
| Series / family | Halogen-free installation cable |
| Exact model | NHXMH |
| Applications | Public buildings, Emergency circuits, Low-smoke installation projects |

MODEL IDENTIFICATION

| Exact model | Product / variant | Cable category | Catalog model | Configuration |
| --- | --- | --- | --- | --- |
| NHXMH | NHXMH Halogen-Free Sheathed Installation Cable | Halogen-free installation cable | NHXMH | Select from source table |

TECHNICAL SPECIFICATIONS

| Parameter | Specification |
| --- | --- |
| Cable category | Halogen-free installation cable |
| Catalog model | NHXMH |
| Configuration | Select from source table |
| Manufacturer models | NHXMH |
| Test voltage | Column 2: ¦ [V]: [V]_{AC} ¦ 300 / 500 Volt: 2000 ¦ Column 5: |
| Temperature range | Column 2: in motion ¦ [V]: ¦ 300 / 500 Volt: -5°C till +70°C ¦ Column 5: |
| Operating temperature | Column 2: short circuit ¦ [V]: °C ¦ 300 / 500 Volt: 160 ¦ Column 5: |
| Short circuit time | Column 2: max. ¦ [V]: [sec] ¦ 300 / 500 Volt: 5 ¦ Column 5: |
| Bending radius | Column 2: in motion ¦ [V]: x diameter ¦ 300 / 500 Volt: 12 ¦ Column 5: |
| Flammability | Column 2: standard ¦ [V]: ¦ 300 / 500 Volt: EN 50266-2-4 ¦ Column 5: |
| Source parameter | Column 2: ¦ [V]: ¦ 300 / 500 Volt: EN 60332-1 ¦ Column 5:; Column 2: ¦ [V]: ¦ 300 / 500 Volt: IEC 60332-3 Kat.C ¦ Column 5: |

ENGINEERING TABLES

NHXMH · Source Specification Table 1

| Nominal voltage Uo/U | Column 2 | [V] | 300 / 500 Volt | Column 5 |
| --- | --- | --- | --- | --- |
| Test voltage | Not provided | [V]_{AC} | 2000 | Not provided |
| Temperature range | in motion | Not provided | -5°C till +70°C | Not provided |
| Operating temperature | short circuit | °C | 160 | Not provided |
| Short circuit time | max. | [sec] | 5 | Not provided |
| Bending radius | in motion | x diameter | 12 | Not provided |
| Flammability | standard | Not provided | EN 50266-2-4 | Not provided |
| Not provided | Not provided | Not provided | EN 60332-1 | Not provided |
| Not provided | Not provided | Not provided | IEC 60332-3 Kat.C | Not provided |
| Number of cores and nominal cross section mm^2 | Not provided | Copper figurekg/km | Cond. construction (appr. value)mm | Overall diameter appr. mm |
| 2 x 1,5 | Not provided | 30 | 1 x 1,38 | 8,7 |
| 2 x 2,5 | Not provided | 50 | 1 x 1,38 | 9,5 |
| 3 x 1,5 | Not provided | 45 | 1 x 1,38 | 9,1 |
| 3 x 2,5 | Not provided | 75 | 1 x 1,78 | 9,9 |
| 3 x 4 | Not provided | 120 | 1 x 2,25 | 11,2 |
| 3 x 6 | Not provided | 180 | 1 x 2,76 | 12,7 |
| 3 x 10 | Not provided | 300 | 1 x 3,56 | 15,3 |
| 4 x 1,5 | Not provided | 60 | 1 x 1,38 | 9,7 |
| 4 x 2,5 | Not provided | 100 | 1 x 1,78 | 10,6 |
| 4 x 4 | Not provided | 160 | 1 x 2,25 | 12,5 |
| 4 x 6 | Not provided | 240 | 1 x 2,76 | 13,7 |
| 4 x 10 | Not provided | 400 | 1 x 3,56 | 16,5 |
| 4 x 16 RM | Not provided | 640 | 7 x 1,70 | 19,4 |
| 5 x 1,5 | Not provided | 75 | 1 x 1,38 | 10,4 |
| 5 x 2,5 | Not provided | 125 | 1 x 1,78 | 11,5 |
| 5 x 4 | Not provided | 200 | 1 x 2,25 | 13,5 |
| 5 x 6 | Not provided | 300 | 1 x 2,76 | 15,3 |