CABLE & WIRE FOR ELECTRICAL, ELV AND INDUSTRIAL PROJECTS

# H05V-K Flexible PVC Insulated Wire

Models: H05V-K | H07V-K

PRODUCT IMAGES

| H05V-K · Primary | H05V-K · Gallery | H07V-K · Primary | H07V-K · Gallery |
| --- | --- | --- | --- |

PRODUCT OVERVIEW

NexPro H05V-K Flexible PVC Insulated Wire is supplied as a configurable single-core flexible wire product family. Catalog models are preserved exactly as H05V-K. Use the source-derived tables below to select the required conductor construction, core arrangement, cross-section and dimensions.

| Product line | Cable & Wire for Electrical, ELV and Industrial Projects |
| --- | --- |
| Series / family | Single-core flexible wire |
| Exact model | H05V-K ¦ H07V-K |
| Applications | Equipment connections, Flexible wiring, OEM electrical assemblies |

MODEL COMPARISON

| Exact model | Product / variant | Cable category | Catalog model | Configuration |
| --- | --- | --- | --- | --- |
| H05V-K | H05V-K Flexible PVC Insulated Wire | Single-core flexible wire | H05V-K | Select from source table |
| H07V-K | H07V-K Flexible PVC Insulated Wire | Single-core flexible wire | H07V-K | Select from source table |

TECHNICAL SPECIFICATIONS

| Parameter | H05V-K | H07V-K |
| --- | --- | --- |
| Cable category | Single-core flexible wire | Single-core flexible wire |
| Catalog model | H05V-K | H07V-K |
| Configuration | Select from source table | Select from source table |
| Manufacturer models | H05V-K | H07V-K |
| 1x0,5 | Resistance at 20 °C (Ohm/km): 39 ¦ External Diameter (mm): 2,15 ¦ Weight (kg/km): 9 ¦ Class: Eca | Not provided |
| 1x0,75 | Resistance at 20 °C (Ohm/km): 26 ¦ External Diameter (mm): 2,25 ¦ Weight (kg/km): 11 ¦ Class: Eca | Not provided |
| 1x1 | Resistance at 20 °C (Ohm/km): 19,5 ¦ External Diameter (mm): 2,50 ¦ Weight (kg/km): 14 ¦ Class: Eca | Not provided |
| 1.5 | Not provided | Conductor diam. (mm): 1.55 ¦ Nom. o u t e r d i a m . (mm): 3.50 ¦ Permissible current rating (3 conductors) (A): 15.5 ¦ Permissible current (One phase) (A): 17.5 ¦ Approx. weight (kg/km): 21 |
| 2.5 | Not provided | Conductor diam. (mm): 2.00 ¦ Nom. o u t e r d i a m . (mm): 4.2 ¦ Permissible current rating (3 conductors) (A): 21.0 ¦ Permissible current (One phase) (A): 24.0 ¦ Approx. weight (kg/km): 35 |
| 4 | Not provided | Conductor diam. (mm): 2.50 ¦ Nom. o u t e r d i a m . (mm): 4.8 ¦ Permissible current rating (3 conductors) (A): 28.0 ¦ Permissible current (One phase) (A): 32.0 ¦ Approx. weight (kg/km): 45 |
| 6 | Not provided | Conductor diam. (mm): 3.00 ¦ Nom. o u t e r d i a m . (mm): 6.3 ¦ Permissible current rating (3 conductors) (A): 36.0 ¦ Permissible current (One phase) (A): 41.0 ¦ Approx. weight (kg/km): 68 |
| 10 | Not provided | Conductor diam. (mm): 4.00 ¦ Nom. o u t e r d i a m . (mm): 7.6 ¦ Permissible current rating (3 conductors) (A): 50.0 ¦ Permissible current (One phase) (A): 57.0 ¦ Approx. weight (kg/km): 115 |
| 16 | Not provided | Conductor diam. (mm): 5.45 ¦ Nom. o u t e r d i a m . (mm): 8.8 ¦ Permissible current rating (3 conductors) (A): 68.0 ¦ Permissible current (One phase) (A): 76.0 ¦ Approx. weight (kg/km): 183 |
| 25 | Not provided | Conductor diam. (mm): 6.60 ¦ Nom. o u t e r d i a m . (mm): 11.0 ¦ Permissible current rating (3 conductors) (A): 89.0 ¦ Permissible current (One phase) (A): 96.0 ¦ Approx. weight (kg/km): 290 |
| 35 | Not provided | Conductor diam. (mm): 8.00 ¦ Nom. o u t e r d i a m . (mm): 12.5 ¦ Permissible current rating (3 conductors) (A): 110.0 ¦ Permissible current (One phase) (A): 119.0 ¦ Approx. weight (kg/km): 320 |

ENGINEERING TABLES

H05V-K · Source Specification Table 1

| Section (mm²) | Resistance at 20 °C (Ohm/km) | External Diameter (mm) | Weight (kg/km) | Class |
| --- | --- | --- | --- | --- |
| 1x0,5 | 39 | 2,15 | 9 | Eca |
| 1x0,75 | 26 | 2,25 | 11 | Eca |
| 1x1 | 19,5 | 2,50 | 14 | Eca |

H05V-K · Source Specification Table 2

| 1. Conductor | Flexible electrolytic copper conductor (Class V) according to BS EN 60228:2005 (previously BS6360) and EN 60228. |
| --- | --- |
| 2. Insulation | PVC insulation type TI-1 according to BS7655 and HD 21.3S3:1995/A2:2008. |
| Nominal voltage | 300/500 V |
| Test voltage | 2.000 V A.C. |
| Maximum temperature | 70 °C |
| Other characteristics | — |
| Colours according to HD 21.1S4:2002Non-flame propagating according to UNE-EN 60332-1-2, EN 60332-1-2 and IEC 60332-1-2CPR Classification according to EN 50575 | — |

H07V-K · Source Specification Table 1

| Cross section (mm²) | Conductor diam. (mm) | Nom. o u t e r d i a m . (mm) | Permissible current rating (3 conductors) (A) | Permissible current (One phase) (A) | Approx. weight (kg/km) |
| --- | --- | --- | --- | --- | --- |
| 1.5 | 1.55 | 3.50 | 15.5 | 17.5 | 21 |
| 2.5 | 2.00 | 4.2 | 21.0 | 24.0 | 35 |
| 4 | 2.50 | 4.8 | 28.0 | 32.0 | 45 |
| 6 | 3.00 | 6.3 | 36.0 | 41.0 | 68 |
| 10 | 4.00 | 7.6 | 50.0 | 57.0 | 115 |
| 16 | 5.45 | 8.8 | 68.0 | 76.0 | 183 |
| 25 | 6.60 | 11.0 | 89.0 | 96.0 | 290 |
| 35 | 8.00 | 12.5 | 110.0 | 119.0 | 320 |
| 50 | 9.50 | 14.5 | 134.0 | 144.0 | 470 |
| 70 | 11.30 | 17.0 | 171.0 | 184.0 | 505 |
| 95 | 13.60 | 19.0 | 207.0 | 223.0 | 756 |
| 120 | 15.20 | 21.0 | 239.0 | 259.0 | 1120 |
| 150 | 16.70 | 23.5 | 275.0 | 299.0 | 1525 |
| 185 | 18.80 | 26.0 | 315.0 | 341.0 | 1890 |
| 240 | 21.20 | 29.5 | 371.0 | 403.0 | 2340 |