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CABLE & WIRE FOR ELECTRICAL, ELV AND INDUSTRIAL PROJECTS
H05V-K Flexible PVC Insulated Wire
Models: H05V-K | H07V-K
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PRODUCT OVERVIEW
NexPro H05V-K Flexible PVC Insulated Wire is supplied as a configurable single-core flexible wire product family. Catalog models are preserved exactly as H05V-K. Use the source-derived tables below to select the required conductor construction, core arrangement, cross-section and dimensions.
	Product line
	Cable & Wire for Electrical, ELV and Industrial Projects

	Series / family
	Single-core flexible wire

	Exact model
	H05V-K | H07V-K

	Applications
	Equipment connections, Flexible wiring, OEM electrical assemblies


MODEL COMPARISON
	Exact model
	Product / variant
	Cable category
	Catalog model
	Configuration

	H05V-K
	H05V-K Flexible PVC Insulated Wire
	Single-core flexible wire
	H05V-K
	Select from source table

	H07V-K
	H07V-K Flexible PVC Insulated Wire
	Single-core flexible wire
	H07V-K
	Select from source table


TECHNICAL SPECIFICATIONS
	Parameter
	H05V-K
	H07V-K

	Cable category
	Single-core flexible wire
	Single-core flexible wire

	Catalog model
	H05V-K
	H07V-K

	Configuration
	Select from source table
	Select from source table

	Manufacturer models
	H05V-K
	H07V-K

	1x0,5
	Resistance at 20 °C
(Ohm/km): 39 | External Diameter (mm): 2,15 | Weight (kg/km): 9 | Class: Eca
	Not provided

	1x0,75
	Resistance at 20 °C
(Ohm/km): 26 | External Diameter (mm): 2,25 | Weight (kg/km): 11 | Class: Eca
	Not provided

	1x1
	Resistance at 20 °C
(Ohm/km): 19,5 | External Diameter (mm): 2,50 | Weight (kg/km): 14 | Class: Eca
	Not provided

	1.5
	Not provided
	Conductor diam.
(mm): 1.55 | Nom. o u t e r d i a m . (mm): 3.50 | Permissible current rating (3 conductors) (A): 15.5 | Permissible current (One phase) (A): 17.5 | Approx. weight (kg/km): 21

	2.5
	Not provided
	Conductor diam.
(mm): 2.00 | Nom. o u t e r d i a m . (mm): 4.2 | Permissible current rating (3 conductors) (A): 21.0 | Permissible current (One phase) (A): 24.0 | Approx. weight (kg/km): 35

	4
	Not provided
	Conductor diam.
(mm): 2.50 | Nom. o u t e r d i a m . (mm): 4.8 | Permissible current rating (3 conductors) (A): 28.0 | Permissible current (One phase) (A): 32.0 | Approx. weight (kg/km): 45

	6
	Not provided
	Conductor diam.
(mm): 3.00 | Nom. o u t e r d i a m . (mm): 6.3 | Permissible current rating (3 conductors) (A): 36.0 | Permissible current (One phase) (A): 41.0 | Approx. weight (kg/km): 68

	10
	Not provided
	Conductor diam.
(mm): 4.00 | Nom. o u t e r d i a m . (mm): 7.6 | Permissible current rating (3 conductors) (A): 50.0 | Permissible current (One phase) (A): 57.0 | Approx. weight (kg/km): 115

	16
	Not provided
	Conductor diam.
(mm): 5.45 | Nom. o u t e r d i a m . (mm): 8.8 | Permissible current rating (3 conductors) (A): 68.0 | Permissible current (One phase) (A): 76.0 | Approx. weight (kg/km): 183

	25
	Not provided
	Conductor diam.
(mm): 6.60 | Nom. o u t e r d i a m . (mm): 11.0 | Permissible current rating (3 conductors) (A): 89.0 | Permissible current (One phase) (A): 96.0 | Approx. weight (kg/km): 290

	35
	Not provided
	Conductor diam.
(mm): 8.00 | Nom. o u t e r d i a m . (mm): 12.5 | Permissible current rating (3 conductors) (A): 110.0 | Permissible current (One phase) (A): 119.0 | Approx. weight (kg/km): 320


ENGINEERING TABLES
H05V-K · Source Specification Table 1
	Section (mm²)
	Resistance at 20 °C (Ohm/km)
	External Diameter (mm)
	Weight (kg/km)
	Class

	1x0,5
	39
	2,15
	9
	Eca

	1x0,75
	26
	2,25
	11
	Eca

	1x1
	19,5
	2,50
	14
	Eca


H05V-K · Source Specification Table 2
	1. Conductor
	Flexible electrolytic copper conductor (Class V) according to BS EN 60228:2005 (previously BS6360) and EN 60228.

	2. Insulation
	PVC insulation type TI-1 according to BS7655 and HD 21.3S3:1995/A2:2008.

	Nominal voltage
	300/500 V

	Test voltage
	2.000 V A.C.

	Maximum temperature
	70 °C

	Other characteristics
	—

	Colours according to HD 21.1S4:2002Non-flame propagating according to UNE-EN 60332-1-2, EN 60332-1-2 and IEC 60332-1-2CPR Classification according to EN 50575
	—


H07V-K · Source Specification Table 1
	Cross section (mm²)
	Conductor diam. (mm)
	Nom. o u t e r d i a m . (mm)
	Permissible current rating (3 conductors) (A)
	Permissible current (One phase) (A)
	Approx. weight (kg/km)

	1.5
	1.55
	3.50
	15.5
	17.5
	21

	2.5
	2.00
	4.2
	21.0
	24.0
	35

	4
	2.50
	4.8
	28.0
	32.0
	45

	6
	3.00
	6.3
	36.0
	41.0
	68

	10
	4.00
	7.6
	50.0
	57.0
	115

	16
	5.45
	8.8
	68.0
	76.0
	183

	25
	6.60
	11.0
	89.0
	96.0
	290

	35
	8.00
	12.5
	110.0
	119.0
	320

	50
	9.50
	14.5
	134.0
	144.0
	470

	70
	11.30
	17.0
	171.0
	184.0
	505

	95
	13.60
	19.0
	207.0
	223.0
	756

	120
	15.20
	21.0
	239.0
	259.0
	1120

	150
	16.70
	23.5
	275.0
	299.0
	1525

	185
	18.80
	26.0
	315.0
	341.0
	1890

	240
	21.20
	29.5
	371.0
	403.0
	2340
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