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	PRODUCT SPECIFICATION
NHXH E90 Halogen-Free Fire-Resistant Cable
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CABLE & WIRE FOR ELECTRICAL, ELV AND INDUSTRIAL PROJECTS
NHXH E90 Halogen-Free Fire-Resistant Cable
Exact model: NHXH E90
PRODUCT IMAGES
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	NHXH E90 · Primary



PRODUCT OVERVIEW
NexPro NHXH E90 Halogen-Free Fire-Resistant Cable is supplied as a configurable fire-resistant safety cable product family. Catalog models are preserved exactly as NHXH E90. Use the source-derived tables below to select the required conductor construction, core arrangement, cross-section and dimensions.
	Product line
	Cable & Wire for Electrical, ELV and Industrial Projects

	Series / family
	Fire-resistant safety cable

	Exact model
	NHXH E90

	Applications
	Public buildings, Emergency circuits, Low-smoke installation projects


MODEL IDENTIFICATION
	Exact model
	Product / variant
	Cable category
	Catalog model
	Configuration

	NHXH E90
	NHXH E90 Halogen-Free Fire-Resistant Cable
	Fire-resistant safety cable
	NHXH E90
	Select from source table


TECHNICAL SPECIFICATIONS
	Parameter
	Specification

	Cable category
	Fire-resistant safety cable

	Catalog model
	NHXH E90

	Configuration
	Select from source table

	Manufacturer models
	NHXH E90

	Test voltage
	Column 2:  | [V]: [V]_{AC} | 600 / 1000 Volt: 4000

	Temperature range
	Column 2: in motion | [V]:  | 600 / 1000 Volt: -5°C till +90°C

	Operating temperature
	Column 2: short circuit | [V]: °C | 600 / 1000 Volt: 250

	Short circuit time
	Column 2: max. | [V]: [sec] | 600 / 1000 Volt: 5

	Bending radius
	Column 2: single core style | [V]: x diameter | 600 / 1000 Volt: 15

	multi core style
	Column 2: x diameter | [V]: 12 | 600 / 1000 Volt: —

	Flammability
	Column 2: standard | [V]:  | 600 / 1000 Volt: EN 50266-2-4IEC 60332-3 Kat.C


ENGINEERING TABLES
NHXH E90 · Source Specification Table 1
	Nominal voltage Uo/U
	Column 2
	[V]
	600 / 1000 Volt

	Test voltage
	Not provided
	[V]_{AC}
	4000

	Temperature range
	in motion
	Not provided
	-5°C till +90°C

	Operating temperature
	short circuit
	°C
	250

	Short circuit time
	max.
	[sec]
	5

	Bending radius
	single core style
	x diameter
	15

	multi core style
	x diameter
	12
	—

	Flammability
	standard
	Not provided
	EN 50266-2-4IEC 60332-3 Kat.C


NHXH E90 · Source Specification Table 2
	Number of cores and nominal cross section mm^2
	Copper figure kg/km
	Overall diameter appr.mm
	Calorific potential kWh/m
	Weight appr. kg/km

	1 x 16 RM
	160
	10,5
	0,42
	250

	1 x 25 RM
	250
	12,5
	0,53
	355

	1 x 35 RM
	350
	13,5
	0,60
	460

	1 x 50 RM
	500
	15,0
	0,69
	596

	1 x 70 RM
	700
	16,5
	0,83
	810

	1 x 95 RM
	950
	19,0
	1,06
	1.100

	1 x 120 RM
	1.200
	20,5
	1,15
	1.350
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