CABLE & WIRE FOR ELECTRICAL, ELV AND INDUSTRIAL PROJECTS

# NYY 0.6/1 kV PVC Power Cable

Models: NYY | N2XY-J | N2XY-O | N2XY-JZ | N2XY-OZ | VV

PRODUCT IMAGES

| NYY · Primary | NYY · Gallery | N2XY-J ¦ N2XY-O ¦ N2XY-JZ ¦ N2XY-OZ · Primary | VV · Primary |
| --- | --- | --- | --- |

PRODUCT OVERVIEW

NexPro NYY 0.6/1 kV PVC Power Cable is supplied as a configurable low-voltage power cable product family. Catalog models are preserved exactly as NYY. Use the source-derived tables below to select the required conductor construction, core arrangement, cross-section and dimensions.

| Product line | Cable & Wire for Electrical, ELV and Industrial Projects |
| --- | --- |
| Series / family | Low-voltage power cable |
| Exact model | NYY ¦ N2XY-J ¦ N2XY-O ¦ N2XY-JZ ¦ N2XY-OZ ¦ VV |
| Applications | Low-voltage distribution, Industrial power projects, Fixed and buried installations |

MODEL COMPARISON

| Exact model | Product / variant | Cable category | Catalog model | Configuration |
| --- | --- | --- | --- | --- |
| NYY | NYY 0.6/1 kV PVC Power Cable | Low-voltage power cable | NYY | Select from source table |
| N2XY-J ¦ N2XY-O ¦ N2XY-JZ ¦ N2XY-OZ | N2XY 0.6/1 kV XLPE/PVC Power Cable | Low-voltage power cable | N2XY-J ¦ N2XY-O ¦ N2XY-JZ ¦ N2XY-OZ | Select from source table |
| VV | VV PVC Insulated PVC Sheathed Power Cable | Low-voltage power cable | VV | Select from source table |

TECHNICAL SPECIFICATIONS

| Parameter | NYY | N2XY-J ¦ N2XY-O ¦ N2XY-JZ ¦ N2XY-OZ | VV |
| --- | --- | --- | --- |
| Cable category | Low-voltage power cable | Low-voltage power cable | Low-voltage power cable |
| Catalog model | NYY | N2XY-J ¦ N2XY-O ¦ N2XY-JZ ¦ N2XY-OZ | VV |
| Configuration | Select from source table | Select from source table | Select from source table |
| Manufacturer models | NYY | N2XY-J / N2XY-O / N2XY-JZ / N2XY-OZ | VV |
| Nominal voltage Uo/U | Specified value: ¦ Value 2: [V] ¦ Value 3: 600 / 1000 Volt | Not provided | Not provided |
| Test voltage | Specified value: ¦ Value 2: [V]_{AC} ¦ Value 3: 4000 | Not provided | Not provided |
| Temperature range | Specified value: in motion ¦ Value 2: ¦ Value 3: - 5°C till +70°C | Not provided | Not provided |
| fixed | Specified value: ¦ Value 2: -20°C till +70°C ¦ Value 3: — | Not provided | Not provided |
| Bending radius | Specified value: single-core style ¦ Value 2: x diameter ¦ Value 3: 15 | Not provided | Not provided |
| multi-core style | Specified value: x diameter ¦ Value 2: 12 ¦ Value 3: — | Not provided | Not provided |
| Flammability | Specified value: standard ¦ Value 2: ¦ Value 3: EN 60332-1-2 | Not provided | Not provided |
| Source parameter | Not provided | With protective conductor: N2XY-J ¦ Without protective conductor: N2XY-O; With protective conductor: N2XY-JZ ¦ Without protective conductor: N2XY-OZ | Not provided |
| 1 | Not provided | With protective conductor: gn/ye ¦ Without protective conductor: bk | Not provided |
| 2 | Not provided | With protective conductor: - ¦ Without protective conductor: bu, bn | Not provided |
| 3 | Not provided | With protective conductor: gn/ye, bu, bn ¦ Without protective conductor: bn, bk, gy | Not provided |
| 4 | Not provided | With protective conductor: gn/ye, bn, bk, gy ¦ Without protective conductor: bu, bn, bk, gy | Not provided |
| 5 | Not provided | With protective conductor: gn/ye, bu, bn, bk, gy ¦ Without protective conductor: bu, bn, bk, gy, bk | Not provided |
| >5 | Not provided | With protective conductor: gn/ye, black cores with white numbering ¦ Without protective conductor: black cores with white numbering | Not provided |
| Specification status | Not provided | Not provided | No numeric source table was published for this product family |
| Selection guidance | Not provided | Not provided | Confirm the exact model, voltage rating, conductor or core configuration, cross-section, installation conditions, required length and applicable project requirements in the RFQ. |

ENGINEERING TABLES

NYY · Technical data:

| Parameter | Specified value | Value 2 | Value 3 |
| --- | --- | --- | --- |
| Nominal voltage Uo/U | Not provided | [V] | 600 / 1000 Volt |
| Test voltage | Not provided | [V]_{AC} | 4000 |
| Temperature range | in motion | Not provided | - 5°C till +70°C |
| fixed | Not provided | -20°C till +70°C | — |
| Bending radius | single-core style | x diameter | 15 |
| multi-core style | x diameter | 12 | — |
| Flammability | standard | Not provided | EN 60332-1-2 |

NYY · Source Specification Table 2

| Number of cores and nominal cross section | Copper figure | Overall diameter | Weight | Current carrying capacity ground | Current carrying capacity air |
| --- | --- | --- | --- | --- | --- |
| mm^2 | kg/km | appr. mm | kg/km | A | A |
| 1 x 4 RE | 38,4 | 8 | 120 | 50 | 37 |
| 1 x 6 RE | 57,6 | 9 | 131 | 62 | 47 |
| 1 x 10 RE | 96,0 | 10 | 171 | 83 | 64 |
| 1 x 16 RE | 153,6 | 11 | 233 | 107 | 84 |
| 1 x 25 RM | 240,0 | 12 | 370 | 138 | 114 |
| 1 x 35 RM | 336,0 | 14 | 480 | 164 | 139 |
| 1 x 50 RM | 480,0 | 16 | 640 | 195 | 169 |
| 1 x 70 RM | 672,0 | 17 | 850 | 238 | 213 |
| 1 x 95 RM | 912,0 | 19 | 1.120 | 286 | 264 |
| 1 x 120 RM | 1.152,0 | 21 | 1.375 | 325 | 307 |
| 1 x 150 RM | 1.440,0 | 23 | 1.660 | 365 | 352 |
| 1 x 185 RM | 1.776,0 | 25 | 2.050 | 413 | 406 |
| 1 x 240 RM | 2.304,0 | 28 | 2.634 | 479 | 483 |
| 1 x 300 RM | 2.880,0 | 30 | 3.295 | 541 | 557 |

N2XY-J | N2XY-O | N2XY-JZ | N2XY-OZ · Source Specification Table 1

| Number of cores | With protective conductor | Without protective conductor |
| --- | --- | --- |
| Not provided | N2XY-J | N2XY-O |
| 1 | gn/ye | bk |
| 2 | - | bu, bn |
| 3 | gn/ye, bu, bn | bn, bk, gy |
| 4 | gn/ye, bn, bk, gy | bu, bn, bk, gy |
| 5 | gn/ye, bu, bn, bk, gy | bu, bn, bk, gy, bk |
| Not provided | N2XY-JZ | N2XY-OZ |
| >5 | gn/ye, black cores with white numbering | black cores with white numbering |