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UPS UNINTERRUPTIBLE POWER SUPPLY
C Series Online Double-Conversion UPS
Exact model: C-SERIES-ONLINE-UPS
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	C-SERIES-ONLINE-UPS · Primary



PRODUCT OVERVIEW
C Series Online Double-Conversion UPS with 9 source-reviewed models for Servers, network rooms, CCTV control rooms and communication systems. Model configuration and destination-market requirements are confirmed during RFQ review.
	Product line
	UPS Uninterruptible Power Supply

	Series / family
	Standalone model

	Exact model
	C-SERIES-ONLINE-UPS

	Applications
	Servers, network rooms, CCTV control rooms and communication systems


MODEL IDENTIFICATION
	Exact model
	Product / variant
	Topology
	Power Range
	Phase

	C-SERIES-ONLINE-UPS
	C Series Online Double-Conversion UPS
	Online UPS
	1000VA / 800W Standard Battery to 10kVA / 8kW Long-Run
	Single phase input / Single phase output


TECHNICAL SPECIFICATIONS
	Parameter
	Specification

	Topology
	Online UPS

	Power Range
	1000VA / 800W Standard Battery to 10kVA / 8kW Long-Run

	Phase
	Single phase input / Single phase output

	Form Factor
	Tower

	Waveform
	Pure sine wave

	Power Factor
	Model-specific; confirm on quotation

	Battery Types
	Model-dependent

	SKU
	C-SERIES-ONLINE-UPS

	Available Configurations
	C1K-STANDARD; C1KS-LONG-RUN; C2K-STANDARD; C2KS-LONG-RUN; C3K-STANDARD; C3KS-LONG-RUN; C5K-STANDARD; C6KS-LONG-RUN; C10KS-LONG-RUN

	Exact Configuration
	Confirm one listed configuration during RFQ review

	Destination Requirements
	To be confirmed


ENGINEERING TABLES
C-SERIES-ONLINE-UPS · Complete Model Specifications — C1K-STANDARD | C1KS-LONG-RUN | C2K-STANDARD | C2KS-LONG-RUN
	Parameter
	C1K-STANDARD
	C1KS-LONG-RUN
	C2K-STANDARD
	C2KS-LONG-RUN

	Rated capacity
	1000VA / 800W Standard Battery
	1000VA / 800W Long-Run
	2000VA / 1600W Standard Battery
	2000VA / 1600W Long-Run

	Battery configuration
	2 × 12V 7Ah
	3 × 12V external batteries; Ah selected by project
	4 × 12V 7Ah
	6 × 12V external batteries; Ah selected by project

	Dimensions
	360 × 147 × 220 mm
	360 × 147 × 220 mm
	440 × 192 × 340 mm
	440 × 192 × 340 mm

	Net weight
	11.9 kg
	8.5 kg
	22 kg
	16 kg

	Transfer time
	0 ms
	0 ms
	0 ms
	0 ms

	Efficiency
	Not provided
	Not provided
	Not provided
	Not provided

	Model configuration — Rated capacity
	1000VA / 800W Standard Battery
	1000VA / 800W Long-Run
	2000VA / 1600W Standard Battery
	2000VA / 1600W Long-Run

	Model configuration — Battery configuration
	2 × 12V 7Ah
	3 × 12V external batteries; Ah selected by project
	4 × 12V 7Ah
	6 × 12V external batteries; Ah selected by project

	Model configuration — Product dimensions
	360 × 147 × 220 mm
	360 × 147 × 220 mm
	440 × 192 × 340 mm
	440 × 192 × 340 mm

	Model configuration — Net weight
	11.9 kg
	8.5 kg
	22 kg
	16 kg

	Model configuration — Transfer time
	0 ms
	0 ms
	0 ms
	0 ms

	Technical Data — Topology
	Online UPS
	Online UPS
	Online UPS
	Online UPS

	Technical Data — Output voltage
	220 VAC
	220 VAC
	220 VAC
	220 VAC

	Technical Data — AC voltage regulation
	±10%
	±10%
	±10%
	±10%

	Technical Data — Battery-mode frequency
	50 Hz ±0.25 Hz or 60 Hz ±0.3 Hz
	50 Hz ±0.25 Hz or 60 Hz ±0.3 Hz
	50 Hz ±0.25 Hz or 60 Hz ±0.3 Hz
	50 Hz ±0.25 Hz or 60 Hz ±0.3 Hz

	Technical Data — Transfer time
	0 ms
	0 ms
	0 ms
	0 ms

	Technical Data — Output waveform
	Pure sine wave
	Pure sine wave
	Pure sine wave
	Pure sine wave

	Technical Data — Overload 105–110%
	Alarm, no shutdown
	Alarm, no shutdown
	Alarm, no shutdown
	Alarm, no shutdown

	Technical Data — Overload 110–130%
	Auto shutdown after 30 seconds
	Auto shutdown after 30 seconds
	Auto shutdown after 30 seconds
	Auto shutdown after 30 seconds

	Technical Data — Overload >130%
	Immediate shutdown
	Immediate shutdown
	Immediate shutdown
	Immediate shutdown

	Technical Data — Environment
	20–90% RH, 0–40°C, non-condensing
	20–90% RH, 0–40°C, non-condensing
	20–90% RH, 0–40°C, non-condensing
	20–90% RH, 0–40°C, non-condensing

	Technical Data — Noise
	<55 dBA at 1 m
	<55 dBA at 1 m
	<55 dBA at 1 m
	<55 dBA at 1 m

	Technical Data — Management
	RS-232; optional SNMP/web management
	RS-232; optional SNMP/web management
	RS-232; optional SNMP/web management
	RS-232; optional SNMP/web management

	Technical Data — Capacity
	1000VA /800W
	1000VA /800W
	2000VA /1600W
	2000VA /1600W

	Technical Data — Input voltage range
	145–275 VAC ±5V
	145–275 VAC ±5V
	145–275 VAC ±5V
	145–275 VAC ±5V

	Technical Data — Input frequency
	50–60 Hz
	50–60 Hz
	50–60 Hz
	50–60 Hz

	Technical Data — Battery configuration
	2 × 12V 7Ah
	3 × 12V external batteries; Ah selected by project
	4 × 12V 7Ah
	6 × 12V external batteries; Ah selected by project

	Technical Data — Maximum charging current
	1A ±10%; optional max. 1A or 2A
	>5 A
	1A ±10%; optional max. 1A or 2A
	>5 A

	Technical Data — Charging voltage
	27.3 VDC ±1%
	27.4 VDC ±1%
	54.7 VDC ±1%
	82.1 VDC ±1%

	Technical Data — Dimensions
	360 × 147 × 220 mm
	360 × 147 × 220 mm
	440 × 192 × 340 mm
	440 × 192 × 340 mm

	Technical Data — Net weight
	11.9 kg
	8.5 kg
	22 kg
	16 kg


C-SERIES-ONLINE-UPS · Complete Model Specifications — C3K-STANDARD | C3KS-LONG-RUN | C5K-STANDARD | C6KS-LONG-RUN
	Parameter
	C3K-STANDARD
	C3KS-LONG-RUN
	C5K-STANDARD
	C6KS-LONG-RUN

	Rated capacity
	3000VA / 2400W Standard Battery
	3000VA / 2400W Long-Run
	5000VA / 3000W Standard Battery
	6000VA / 4.8kW Long-Run

	Battery configuration
	6 × 12V 7Ah
	8 × 12V external batteries; Ah selected by project
	4 × 12V 17Ah
	16 × 12V external batteries; Ah selected by project

	Dimensions
	440 × 192 × 340 mm
	440 × 192 × 340 mm
	440 × 190 × 320 mm
	520 × 240 × 460 mm

	Net weight
	27.9 kg
	18.2 kg
	33 kg
	30.5 kg

	Transfer time
	0 ms
	0 ms
	0 ms
	0 ms

	Efficiency
	Not provided
	Not provided
	Not provided
	Not provided

	Model configuration — Rated capacity
	3000VA / 2400W Standard Battery
	3000VA / 2400W Long-Run
	5000VA / 3000W Standard Battery
	6000VA / 4.8kW Long-Run

	Model configuration — Battery configuration
	6 × 12V 7Ah
	8 × 12V external batteries; Ah selected by project
	4 × 12V 17Ah
	16 × 12V external batteries; Ah selected by project

	Model configuration — Product dimensions
	440 × 192 × 340 mm
	440 × 192 × 340 mm
	440 × 190 × 320 mm
	520 × 240 × 460 mm

	Model configuration — Net weight
	27.9 kg
	18.2 kg
	33 kg
	30.5 kg

	Model configuration — Transfer time
	0 ms
	0 ms
	0 ms
	0 ms

	Technical Data — Topology
	Online UPS
	Online UPS
	Online UPS
	Online UPS

	Technical Data — Output voltage
	220 VAC
	220 VAC
	220 VAC
	220 VAC

	Technical Data — AC voltage regulation
	±10%
	±10%
	±10%
	±10%

	Technical Data — Battery-mode frequency
	50 Hz ±0.25 Hz or 60 Hz ±0.3 Hz
	50 Hz ±0.25 Hz or 60 Hz ±0.3 Hz
	50 Hz ±0.25 Hz or 60 Hz ±0.3 Hz
	50 Hz ±0.25 Hz or 60 Hz ±0.3 Hz

	Technical Data — Transfer time
	0 ms
	0 ms
	0 ms
	0 ms

	Technical Data — Output waveform
	Pure sine wave
	Pure sine wave
	Pure sine wave
	Pure sine wave

	Technical Data — Overload 105–110%
	Alarm, no shutdown
	Alarm, no shutdown
	Alarm, no shutdown
	Alarm, no shutdown

	Technical Data — Overload 110–130%
	Auto shutdown after 30 seconds
	Auto shutdown after 30 seconds
	Auto shutdown after 30 seconds
	Auto shutdown after 30 seconds

	Technical Data — Overload >130%
	Immediate shutdown
	Immediate shutdown
	Immediate shutdown
	Immediate shutdown

	Technical Data — Environment
	20–90% RH, 0–40°C, non-condensing
	20–90% RH, 0–40°C, non-condensing
	20–90% RH, 0–40°C, non-condensing
	20–90% RH, 0–40°C, non-condensing

	Technical Data — Noise
	<55 dBA at 1 m
	<55 dBA at 1 m
	<55 dBA at 1 m
	<55 dBA at 1 m

	Technical Data — Management
	RS-232; optional SNMP/web management
	RS-232; optional SNMP/web management
	RS-232; optional SNMP/web management
	RS-232; optional SNMP/web management

	Technical Data — Capacity
	3000VA /2400W
	3000VA /2400W
	5000VA /3000W
	6000VA /4.8kW

	Technical Data — Input voltage range
	145–275 VAC ±5V
	145–275 VAC ±5V
	165–275 VAC ±5V
	165–275 VAC ±5V

	Technical Data — Input frequency
	50–60 Hz
	50–60 Hz
	50–60 Hz
	50–60 Hz

	Technical Data — Battery configuration
	6 × 12V 7Ah
	8 × 12V external batteries; Ah selected by project
	4 × 12V 17Ah
	16 × 12V external batteries; Ah selected by project

	Technical Data — Maximum charging current
	1A ±10%; optional max. 1A or 2A
	>5 A
	1A ±10%; optional max. 1A or 2A
	>5 A

	Technical Data — Charging voltage
	82.0 VDC ±1%
	109.4 VDC ±1%
	54.7 VDC ±1%
	218.4 VDC ±1%

	Technical Data — Dimensions
	440 × 192 × 340 mm
	440 × 192 × 340 mm
	440 × 190 × 320 mm
	520 × 240 × 460 mm

	Technical Data — Net weight
	27.9 kg
	18.2 kg
	33 kg
	30.5 kg


C-SERIES-ONLINE-UPS · Complete Model Specifications — C10KS-LONG-RUN
	Parameter
	C10KS-LONG-RUN

	Rated capacity
	10kVA / 8kW Long-Run

	Battery configuration
	16 × 12V external batteries; Ah selected by project

	Dimensions
	520 × 240 × 460 mm

	Net weight
	35 kg

	Transfer time
	0 ms

	Efficiency
	Not provided

	Model configuration — Rated capacity
	10kVA / 8kW Long-Run

	Model configuration — Battery configuration
	16 × 12V external batteries; Ah selected by project

	Model configuration — Product dimensions
	520 × 240 × 460 mm

	Model configuration — Net weight
	35 kg

	Model configuration — Transfer time
	0 ms

	Technical Data — Topology
	Online UPS

	Technical Data — Output voltage
	220 VAC

	Technical Data — AC voltage regulation
	±10%

	Technical Data — Battery-mode frequency
	50 Hz ±0.25 Hz or 60 Hz ±0.3 Hz

	Technical Data — Transfer time
	0 ms

	Technical Data — Output waveform
	Pure sine wave

	Technical Data — Overload 105–110%
	Alarm, no shutdown

	Technical Data — Overload 110–130%
	Auto shutdown after 30 seconds

	Technical Data — Overload >130%
	Immediate shutdown

	Technical Data — Environment
	20–90% RH, 0–40°C, non-condensing

	Technical Data — Noise
	<55 dBA at 1 m

	Technical Data — Management
	RS-232; optional SNMP/web management

	Technical Data — Capacity
	10kVA /8kW

	Technical Data — Input voltage range
	165–275 VAC ±5V

	Technical Data — Input frequency
	50–60 Hz

	Technical Data — Battery configuration
	16 × 12V external batteries; Ah selected by project

	Technical Data — Maximum charging current
	>5 A

	Technical Data — Charging voltage
	218.4 VDC ±1%

	Technical Data — Dimensions
	520 × 240 × 460 mm

	Technical Data — Net weight
	35 kg
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