UPS UNINTERRUPTIBLE POWER SUPPLY

# 3-Phase Low Frequency UPS 10KVA-800KVA Series

Exact model: NX-UP-3P-002

PRODUCT IMAGES

| NX-UP-3P-002 · Primary | NX-UP-3P-002 · Gallery |
| --- | --- |

PRODUCT OVERVIEW

Industrial-grade three-phase low frequency UPS with built-in output isolation transformer. Seven model variants from 10KVA to 800KVA for harsh environments and heavy industrial loads.

| Product line | UPS Uninterruptible Power Supply |
| --- | --- |
| Series / family | Standalone model |
| Exact model | NX-UP-3P-002 |
| Applications | Heavy industrial facilities, Large data centers, Manufacturing plants, Power grid substations, Oil and gas installations, Transportation hubs |

MODEL IDENTIFICATION

| Exact model | Product / variant | Topology | Power Range | Phase |
| --- | --- | --- | --- | --- |
| NX-UP-3P-002 | 3-Phase Low Frequency UPS 10KVA-800KVA Series | Online Double Conversion with Isolation Transformer | 10KVA-800KVA / 8KW-640KW | 3-phase + N input / 3-phase + N output |

TECHNICAL SPECIFICATIONS

| Parameter | Specification |
| --- | --- |
| Topology | Online Double Conversion with Isolation Transformer |
| Power Range | 10KVA-800KVA / 8KW-640KW |
| Phase | 3-phase + N input / 3-phase + N output |
| Form Factor | Floor-standing |
| Waveform | Pure sine wave |
| Power Factor | 0.8 |
| Battery Types | External VRLA battery bank (32×12VDC) |
| SKU | NX-UP-3P-002 |
| Available Configurations | 3C33 10KS; 3C33 20KS; 3C33 30KS; 3C33 40KS; 3C33 60KS; 3C33 80KS; 3C33 100-800KS |
| Exact Configuration | Confirm one listed configuration during RFQ review |
| Destination Requirements | To be confirmed |

ENGINEERING TABLES

NX-UP-3P-002 · Complete Model Specifications — 3C33 10KS | 3C33 20KS | 3C33 30KS | 3C33 40KS

| Parameter | 3C33 10KS | 3C33 20KS | 3C33 30KS | 3C33 40KS |
| --- | --- | --- | --- | --- |
| Rated capacity | 10KVA / 8KW | 20KVA / 16KW | 30KVA / 24KW | 40KVA / 32KW |
| Battery configuration | External 32×12VDC (384VDC) | External 32×12VDC (384VDC) | External 32×12VDC (384VDC) | External 32×12VDC (384VDC) |
| Dimensions | 653×405×820mm | 653×405×820mm | 820×433×1160mm | 820×433×1160mm |
| Net weight | 120kg | 136kg | 242kg | 249kg |
| Transfer time | 0ms | 0ms | 0ms | 0ms |
| Efficiency | AC: 90% / Battery: 90% | AC: 90% / Battery: 90% | AC: 91% / Battery: 91% | AC: 91% / Battery: 91% |
| Model configuration — Rated capacity | 10KVA / 8KW | 20KVA / 16KW | 30KVA / 24KW | 40KVA / 32KW |
| Model configuration — Battery configuration | External 32×12VDC (384VDC) | External 32×12VDC (384VDC) | External 32×12VDC (384VDC) | External 32×12VDC (384VDC) |
| Model configuration — Product dimensions | 653×405×820mm | 653×405×820mm | 820×433×1160mm | 820×433×1160mm |
| Model configuration — Net weight | 120kg | 136kg | 242kg | 249kg |
| Model configuration — Transfer time | 0ms | 0ms | 0ms | 0ms |
| Model configuration — Efficiency | AC: 90% / Battery: 90% | AC: 90% / Battery: 90% | AC: 91% / Battery: 91% | AC: 91% / Battery: 91% |
| Input — Input voltage | 3×380/400/415VAC (3ph+N) | 3×380/400/415VAC (3ph+N) | 3×380/400/415VAC (3ph+N) | 3×380/400/415VAC (3ph+N) |
| Input — Input voltage range | 304–456VAC | 304–456VAC | 304–456VAC | 304–456VAC |
| Input — Input frequency | 50Hz ±10% | 50Hz ±10% | 50Hz ±10% | 50Hz ±10% |
| Output — Output voltage | 3×380/400/415VAC (3ph+N) | 3×380/400/415VAC (3ph+N) | 3×380/400/415VAC (3ph+N) | 3×380/400/415VAC (3ph+N) |
| Output — Voltage regulation | 1% | 1% | 1% | 1% |
| Output — Output power factor | 0.8 | 0.8 | 0.8 | 0.8 |
| Output — AC-mode frequency | 50/60Hz ±0.01Hz | 50/60Hz ±0.01Hz | 50/60Hz ±0.01Hz | 50/60Hz ±0.01Hz |
| Output — Battery-mode frequency | 50/60Hz ±0.01Hz | 50/60Hz ±0.01Hz | 50/60Hz ±0.01Hz | 50/60Hz ±0.01Hz |
| Output — THD (linear load) | <2% | <2% | <2% | <2% |
| Output — THD (non-linear load) | <5% | <5% | <5% | <5% |
| Output — Overload capacity | ≤110%: 60min; ≤125%: 10min; ≤150%: 1min; >150%: 200ms | ≤110%: 60min; ≤125%: 10min; ≤150%: 1min; >150%: 200ms | ≤110%: 60min; ≤125%: 10min; ≤150%: 1min; >150%: 200ms | ≤110%: 60min; ≤125%: 10min; ≤150%: 1min; >150%: 200ms |
| Bypass — Bypass type | Static switch | Static switch | Static switch | Static switch |
| Bypass — Bypass voltage | 3×380/400/415VAC (3ph+N) | 3×380/400/415VAC (3ph+N) | 3×380/400/415VAC (3ph+N) | 3×380/400/415VAC (3ph+N) |
| Bypass — Bypass frequency | 50/60Hz | 50/60Hz | 50/60Hz | 50/60Hz |
| Bypass — Control mode | Microprocessor control | Microprocessor control | Microprocessor control | Microprocessor control |
| Bypass — Transfer time | 0ms | 0ms | 0ms | 0ms |
| Bypass — Switch to bypass | Immediate at 160% overload | Immediate at 160% overload | Immediate at 160% overload | Immediate at 160% overload |
| Bypass — Return from bypass | Automatic after alarm clearing | Automatic after alarm clearing | Automatic after alarm clearing | Automatic after alarm clearing |
| Bypass — Maintenance bypass | Uninterrupted; 3×400V (3ph+N); 50/60Hz | Uninterrupted; 3×400V (3ph+N); 50/60Hz | Uninterrupted; 3×400V (3ph+N); 50/60Hz | Uninterrupted; 3×400V (3ph+N); 50/60Hz |
| Charging — Battery quantity | 32 × 12VDC; 29–32 adjustable | 32 × 12VDC; 29–32 adjustable | 32 × 12VDC; 29–32 adjustable | 32 × 12VDC; 29–32 adjustable |
| Charging — Rated battery voltage | 384VDC | 384VDC | 384VDC | 384VDC |
| Charging — Charging method | CC/CV | CC/CV | CC/CV | CC/CV |
| Charging — Charging voltage | 432VDC; based on 32 batteries | 432VDC; based on 32 batteries | 432VDC; based on 32 batteries | 432VDC; based on 32 batteries |

NX-UP-3P-002 · Complete Model Specifications — 3C33 60KS | 3C33 80KS | 3C33 100-800KS

| Parameter | 3C33 60KS | 3C33 80KS | 3C33 100-800KS |
| --- | --- | --- | --- |
| Rated capacity | 60KVA / 48KW | 80KVA / 64KW | 100KVA-800KVA / 80KW-640KW |
| Battery configuration | External 32×12VDC (384VDC) | External 32×12VDC (384VDC) | External 32×12VDC (384VDC) |
| Dimensions | 820×433×1160mm | 975×635×1325mm | Not provided |
| Net weight | 290kg | 419kg | Not provided |
| Transfer time | 0ms | 0ms | 0ms |
| Efficiency | AC: 92% / Battery: 93% | AC: 92% / Battery: 93% | AC: 93% / Battery: 93% |
| Model configuration — Rated capacity | 60KVA / 48KW | 80KVA / 64KW | 100KVA-800KVA / 80KW-640KW |
| Model configuration — Battery configuration | External 32×12VDC (384VDC) | External 32×12VDC (384VDC) | External 32×12VDC (384VDC) |
| Model configuration — Product dimensions | 820×433×1160mm | 975×635×1325mm | Not provided |
| Model configuration — Net weight | 290kg | 419kg | Not provided |
| Model configuration — Transfer time | 0ms | 0ms | 0ms |
| Model configuration — Efficiency | AC: 92% / Battery: 93% | AC: 92% / Battery: 93% | AC: 93% / Battery: 93% |
| Input — Input voltage | 3×380/400/415VAC (3ph+N) | 3×380/400/415VAC (3ph+N) | 3×380/400/415VAC (3ph+N) |
| Input — Input voltage range | 304–456VAC | 304–456VAC | 304–456VAC |
| Input — Input frequency | 50Hz ±10% | 50Hz ±10% | 50Hz ±10% |
| Output — Output voltage | 3×380/400/415VAC (3ph+N) | 3×380/400/415VAC (3ph+N) | 3×380/400/415VAC (3ph+N) |
| Output — Voltage regulation | 1% | 1% | 1% |
| Output — Output power factor | 0.8 | 0.8 | 0.8 |
| Output — AC-mode frequency | 50/60Hz ±0.01Hz | 50/60Hz ±0.01Hz | 50/60Hz ±0.01Hz |
| Output — Battery-mode frequency | 50/60Hz ±0.01Hz | 50/60Hz ±0.01Hz | 50/60Hz ±0.01Hz |
| Output — THD (linear load) | <2% | <2% | <2% |
| Output — THD (non-linear load) | <5% | <5% | <5% |
| Output — Overload capacity | ≤110%: 60min; ≤125%: 10min; ≤150%: 1min; >150%: 200ms | ≤110%: 60min; ≤125%: 10min; ≤150%: 1min; >150%: 200ms | ≤110%: 60min; ≤125%: 10min; ≤150%: 1min; >150%: 200ms |
| Bypass — Bypass type | Static switch | Static switch | Static switch |
| Bypass — Bypass voltage | 3×380/400/415VAC (3ph+N) | 3×380/400/415VAC (3ph+N) | 3×380/400/415VAC (3ph+N) |
| Bypass — Bypass frequency | 50/60Hz | 50/60Hz | 50/60Hz |
| Bypass — Control mode | Microprocessor control | Microprocessor control | Microprocessor control |
| Bypass — Transfer time | 0ms | 0ms | 0ms |
| Bypass — Switch to bypass | Immediate at 160% overload | Immediate at 160% overload | Immediate at 160% overload |
| Bypass — Return from bypass | Automatic after alarm clearing | Automatic after alarm clearing | Automatic after alarm clearing |
| Bypass — Maintenance bypass | Uninterrupted; 3×400V (3ph+N); 50/60Hz | Uninterrupted; 3×400V (3ph+N); 50/60Hz | Uninterrupted; 3×400V (3ph+N); 50/60Hz |
| Charging — Battery quantity | 32 × 12VDC; 29–32 adjustable | 32 × 12VDC; 29–32 adjustable | 32 × 12VDC; 29–32 adjustable |
| Charging — Rated battery voltage | 384VDC | 384VDC | 384VDC |
| Charging — Charging method | CC/CV | CC/CV | CC/CV |
| Charging — Charging voltage | 432VDC; based on 32 batteries | 432VDC; based on 32 batteries | 432VDC; based on 32 batteries |