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UPS UNINTERRUPTIBLE POWER SUPPLY
High Frequency Online UPS 10KVA-30KVA Series
Exact model: NX-UP-HF-003
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PRODUCT OVERVIEW
Mid-power online UPS series with single/three-phase input flexibility. Four models from 10KVA to 30KVA with external battery bank configuration.
	Product line
	UPS Uninterruptible Power Supply

	Series / family
	Standalone model

	Exact model
	NX-UP-HF-003

	Applications
	Medium server rooms, Network centers, Banking and financial systems, Telecommunications infrastructure, Medical equipment, Industrial control


MODEL IDENTIFICATION
	Exact model
	Product / variant
	Topology
	Power Range
	Phase

	NX-UP-HF-003
	High Frequency Online UPS 10KVA-30KVA Series
	Online Double Conversion
	10KVA–30KVA / 8000W–24000W
	Three phase input / Single phase output


TECHNICAL SPECIFICATIONS
	Parameter
	Specification

	Topology
	Online Double Conversion

	Power Range
	10KVA–30KVA / 8000W–24000W

	Phase
	Three phase input / Single phase output

	Form Factor
	Tower

	Waveform
	Pure sine wave

	Power Factor
	0.8

	Battery Types
	External VRLA battery bank

	SKU
	NX-UP-HF-003

	Available Configurations
	3C10K(S); 3C15K(S); 3C20K(S); 3C30K(S)

	Exact Configuration
	Confirm one listed configuration during RFQ review

	Destination Requirements
	To be confirmed


ENGINEERING TABLES
NX-UP-HF-003 · Complete Model Specifications — 3C10K(S) | 3C15K(S) | 3C20K(S) | 3C30K(S)
	Parameter
	3C10K(S)
	3C15K(S)
	3C20K(S)
	3C30K(S)

	Rated capacity
	10KVA / 8000W
	15KVA / 12000W
	20KVA / 16000W
	30KVA / 24000W

	Battery configuration
	External battery bank
	External battery bank
	External battery bank
	External battery bank

	Dimensions
	Not provided
	Not provided
	Not provided
	Not provided

	Net weight
	Not provided
	Not provided
	Not provided
	Not provided

	Transfer time
	0ms
	0ms
	0ms
	0ms

	Efficiency
	AC: 91%; Battery: 91%
	AC: 91%; Battery: 91%
	AC: 93%; Battery: 92%
	AC: 91%; Battery: 90%

	Model configuration — Rated capacity
	10KVA / 8000W
	15KVA / 12000W
	20KVA / 16000W
	30KVA / 24000W

	Model configuration — Battery configuration
	External battery bank
	External battery bank
	External battery bank
	External battery bank

	Model configuration — Transfer time
	0ms
	0ms
	0ms
	0ms

	Model configuration — Efficiency
	AC: 91%; Battery: 91%
	AC: 91%; Battery: 91%
	AC: 93%; Battery: 92%
	AC: 91%; Battery: 90%

	Input — Input voltage
	380/400/415VAC (3ph+N)
	380/400/415VAC (3ph+N)
	380/400/415VAC (3ph+N)
	380/400/415VAC (3ph+N)

	Input — Input voltage range at 50% load
	190–520VAC
	190–520VAC
	190–520VAC
	190–520VAC

	Input — Input voltage range at 100% load
	305–520VAC
	305–520VAC
	305–520VAC
	305–520VAC

	Input — Input frequency
	46–54Hz / 56–64Hz
	46–54Hz / 56–64Hz
	46–54Hz / 56–64Hz
	46–54Hz / 56–64Hz

	Input — Input power factor
	≥0.8 @100% load
	≥0.8 @100% load
	≥0.8 @100% load
	≥0.8 @100% load

	Output — Output voltage
	208/220/230/240VAC
	208/220/230/240VAC
	208/220/230/240VAC
	208/220/230/240VAC

	Output — Voltage regulation
	±1%
	±1%
	±1%
	±1%

	Output — Synchronized frequency
	46–54Hz / 56–64Hz
	46–54Hz / 56–64Hz
	46–54Hz / 56–64Hz
	46–54Hz / 56–64Hz

	Output — Battery-mode frequency
	50/60Hz ±0.2Hz
	50/60Hz ±0.2Hz
	50/60Hz ±0.2Hz
	50/60Hz ±0.2Hz

	Output — Current crest ratio
	3:1
	3:1
	3:1
	3:1

	Output — THD (linear load)
	≤3%
	≤3%
	≤3%
	≤3%

	Output — THD (non-linear load)
	≤5%
	≤5%
	≤5%
	≤5%

	External battery configuration — Battery quantity
	16–20 (adjustable)
	16–20 (adjustable)
	16–20 (adjustable)
	16–20 (adjustable)

	External battery configuration — Charging current
	4A preset; 1 / 2 / 4 / 6A adjustable
	4A preset; 1 / 2 / 4 / 6A adjustable
	4A preset; 1 / 2 / 4 / 6A adjustable
	4A preset; 1 / 2 / 4 / 6A adjustable

	External battery configuration — Charging voltage
	218.4 / 273VDC ±1%
	218.4 / 273VDC ±1%
	218.4 / 273VDC ±1%
	218.4 / 273VDC ±1%

	Communication & Monitoring — Communication interface
	RS232 / USB
	RS232 / USB
	RS232 / USB
	RS232 / USB

	Communication & Monitoring — SNMP
	Optional
	Optional
	Optional
	Optional

	Communication & Monitoring — Display
	LCD
	LCD
	LCD
	LCD

	Environment — Operating temperature
	0–45°C
	0–45°C
	0–45°C
	0–45°C

	Environment — Relative humidity
	20–95% RH (non-condensing)
	20–95% RH (non-condensing)
	20–95% RH (non-condensing)
	20–95% RH (non-condensing)

	Environment — Noise level
	<60dBA @1m
	<60dBA @1m
	<60dBA @1m
	<60dBA @1m
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3C10K(S) | 3C15K(S) [ 3C20K(S) | 3C30K(S)

- 10KVA 15KVA 20KVA 30KVA
& & Capacity 8000W 12000W 16000W 24000W

fifiz Phase Three-input single-output

i Input

i A HLIE Input voltage 380/400/415VAC(3ph+N)

190-520VAC(3-phase+N)@50% load %%,

[ il Voltage range 305-520VAC(3-phase)@100% load 7

i NAEE Input frequency 46-54Hz or 56-64HZ
3% 5% Power factor 20.8@100% load
4t Output

K1t 1 JE Output voltage 208/220/230/240VAC
5 1% AC voltage regulation +1%
A (R IESE D

Frequency (Synchronous correction range) 46-54Hz/56-64Hz

EZE SN QRS W)

Frequency range (Battery mode) 90Hz/60H=40.2Hz

411 A %4 Surge rating 3:1 (g Kmax)
1k 7 1 % Waveform balance <3% THD(Linear Load 2k 1 1%k ) <5% THD(Non-linear Load £k 1% 71 %% )
A} 4] Transfer time Oms
it Hi 9 7 Output waveform 4li 1 5% Pure Sine Wave
%% Efficiencies
it Mains mode 91% 91% 93% 91%
il Battery mode 91% 91% 92% 90%
KZ4HL External battery UPS
i % Battery model Hy e F H i 7 Depends on the applicant
Kb it Hiil £ Battery number 16-20 adjustable (n[ %)
External % "
UPS IR R 78 L LA e )
baftery Max charging current n 1% Preset 4A, 1] il §21 A/2A/4A adjustable
FoHLHLE
Charding vollage 218.4VDC1%, 273VDC1%
HLo R JU5F Size (MM) 575248620 815250826
Machine
data it Weight (KG) 27 35 35 64

E7R U Display description

LCD TR/, HLibA A, Al B, SRR, MR

Load size, battery capacity, mains mode, battery mode, bypass mode, fault indication

{# F 355 Usage environment

Y% Humidity 20-95%RH@0-45°C (No condensation A<k % )
¥ Noise <60dbA@1M
1% ¥ Control Management
A58 Smart RS-232/USB Y+ Supports Windows®2000/2003/XP/Vista/2008, Windows®7/8, Linux, and MAC
7% Optional SNMP PR B S SNMPA HL 5 o 4 7 3

Power management supports SNMP management and network management
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