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UPS UNINTERRUPTIBLE POWER SUPPLY
Rack-Mounted Online UPS 1KVA-10KVA Series
Exact model: NX-UP-RM-001
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PRODUCT OVERVIEW
19-inch rack-mountable online UPS series with true double conversion. Five models from 1KVA to 10KVA for server cabinet and structured cabling integration.
	Product line
	UPS Uninterruptible Power Supply

	Series / family
	Standalone model

	Exact model
	NX-UP-RM-001

	Applications
	Server racks and cabinets, Network infrastructure, Data centers, Telecommunications, Industrial control systems


MODEL IDENTIFICATION
	Exact model
	Product / variant
	Topology
	Power Range
	Phase

	NX-UP-RM-001
	Rack-Mounted Online UPS 1KVA-10KVA Series
	Online Double Conversion
	1KVA-10KVA / 900W-9000W
	Single phase input / Single phase output


TECHNICAL SPECIFICATIONS
	Parameter
	Specification

	Topology
	Online Double Conversion

	Power Range
	1KVA-10KVA / 900W-9000W

	Phase
	Single phase input / Single phase output

	Form Factor
	19-inch Rack Mount

	Waveform
	Pure sine wave

	Power Factor
	0.9 (1–3kVA); 0.8 (6–10kVA)

	Battery Types
	VRLA sealed lead-acid; External battery (extended runtime)

	SKU
	NX-UP-RM-001

	Available Configurations
	C1KR(S); C2KR(S); C3KR(S); C6KR(S); C10KR(S)

	Exact Configuration
	Confirm one listed configuration during RFQ review

	Destination Requirements
	To be confirmed


ENGINEERING TABLES
NX-UP-RM-001 · Complete Model Specifications — C1KR(S) | C2KR(S) | C3KR(S) | C6KR(S)
	Parameter
	C1KR(S)
	C2KR(S)
	C3KR(S)
	C6KR(S)

	Rated capacity
	1KVA / 900W
	2KVA / 1800W
	3KVA / 2700W
	6KVA / 4800W

	Battery configuration
	Internal VRLA
	Internal VRLA
	Internal VRLA
	Internal VRLA + External option

	Dimensions
	Not provided
	Not provided
	Not provided
	Not provided

	Net weight
	Not provided
	Not provided
	Not provided
	Not provided

	Transfer time
	0ms
	0ms
	0ms
	0ms

	Efficiency
	AC: 92%; Battery: 90%
	AC: 92%; Battery: 90%
	AC: 92%; Battery: 90%
	AC: 92%; Battery: 90%

	Model configuration — Rated capacity
	1KVA / 900W
	2KVA / 1800W
	3KVA / 2700W
	6KVA / 4800W

	Model configuration — Battery configuration
	Internal VRLA
	Internal VRLA
	Internal VRLA
	Internal VRLA + External option

	Model configuration — Transfer time
	0ms
	0ms
	0ms
	0ms

	Model configuration — Efficiency
	AC: 92%; Battery: 90%
	AC: 92%; Battery: 90%
	AC: 92%; Battery: 90%
	AC: 92%; Battery: 90%

	Input — Input voltage
	100/110/115/120/127VAC or 200/208/220/230/240VAC
	100/110/115/120/127VAC or 200/208/220/230/240VAC
	100/110/115/120/127VAC or 200/208/220/230/240VAC
	100/110/115/120/127VAC or 200/208/220/230/240VAC

	Input — Input frequency
	46–54Hz / 56–64Hz
	46–54Hz / 56–64Hz
	46–54Hz / 56–64Hz
	46–54Hz / 56–64Hz

	Input — Input power factor
	≥0.99 @100% load
	≥0.99 @100% load
	≥0.99 @100% load
	≥0.99 @100% load

	Input — Input voltage range at 50% load
	55–145VAC / 110–300VAC
	55–145VAC / 110–300VAC
	55–145VAC / 110–300VAC
	110–300VAC ±3%

	Input — Input voltage range at 100% load
	85–140VAC / 160–280VAC
	85–140VAC / 160–280VAC
	85–140VAC / 160–280VAC
	176–300VAC ±3%

	Output — Output voltage
	100/110/115/120/127VAC or 200/208/220/230/240VAC
	100/110/115/120/127VAC or 200/208/220/230/240VAC
	100/110/115/120/127VAC or 200/208/220/230/240VAC
	100/110/115/120/127VAC or 200/208/220/230/240VAC

	Output — Voltage regulation
	±1%
	±1%
	±1%
	±1%

	Output — Synchronized frequency
	46–54Hz / 56–64Hz
	46–54Hz / 56–64Hz
	46–54Hz / 56–64Hz
	46–54Hz / 56–64Hz

	Output — Current crest ratio
	3:1
	3:1
	3:1
	3:1

	Output — THD (linear load)
	≤3%
	≤3%
	≤3%
	≤3%

	Output — THD (non-linear load)
	≤6%
	≤6%
	≤6%
	≤6%

	Output — Battery-mode frequency
	50Hz ±0.25Hz / 60Hz ±0.3Hz
	50Hz ±0.25Hz / 60Hz ±0.3Hz
	50Hz ±0.25Hz / 60Hz ±0.3Hz
	50/60Hz ±0.1Hz

	Communication & Monitoring — Communication interface
	RS232 / USB
	RS232 / USB
	RS232 / USB
	RS232 / USB

	Communication & Monitoring — SNMP
	Optional
	Optional
	Optional
	Optional

	Communication & Monitoring — Display
	LCD
	LCD
	LCD
	LCD

	Environment — Operating temperature
	0–40°C
	0–40°C
	0–40°C
	0–40°C

	Environment — Relative humidity
	20–90% RH (non-condensing)
	20–90% RH (non-condensing)
	20–90% RH (non-condensing)
	20–90% RH (non-condensing)

	Environment — Noise level
	<50dBA @1m
	<50dBA @1m
	<50dBA @1m
	<50dBA @1m

	External battery configuration — Charging current
	1 / 2 / 4 / 6A (adjustable)
	1 / 2 / 4 / 6A (adjustable)
	1 / 2 / 4 / 6A (adjustable)
	1 / 2 / 4 / 6A (adjustable)

	External battery configuration — Battery quantity
	2 / 3
	4
	6
	16–20 (adjustable)

	External battery configuration — Product dimensions
	400×438×88mm
	400×438×88mm
	400×438×88mm
	400×438×88mm

	External battery configuration — Net weight
	5.6kg
	8.6kg
	8.6kg
	13kg


NX-UP-RM-001 · Complete Model Specifications — C10KR(S)
	Parameter
	C10KR(S)

	Rated capacity
	10KVA / 8000W

	Battery configuration
	Internal VRLA + External option

	Dimensions
	Not provided

	Net weight
	Not provided

	Transfer time
	0ms

	Efficiency
	AC: 93%; Battery: 91%

	Model configuration — Rated capacity
	10KVA / 8000W

	Model configuration — Battery configuration
	Internal VRLA + External option

	Model configuration — Transfer time
	0ms

	Model configuration — Efficiency
	AC: 93%; Battery: 91%

	Input — Input voltage
	100/110/115/120/127VAC or 200/208/220/230/240VAC

	Input — Input frequency
	46–54Hz / 56–64Hz

	Input — Input power factor
	≥0.99 @100% load

	Input — Input voltage range at 50% load
	110–300VAC ±3%

	Input — Input voltage range at 100% load
	176–300VAC ±3%

	Output — Output voltage
	100/110/115/120/127VAC or 200/208/220/230/240VAC

	Output — Voltage regulation
	±1%

	Output — Synchronized frequency
	46–54Hz / 56–64Hz

	Output — Current crest ratio
	3:1

	Output — THD (linear load)
	≤3%

	Output — THD (non-linear load)
	≤6%

	Output — Battery-mode frequency
	50/60Hz ±0.1Hz

	Communication & Monitoring — Communication interface
	RS232 / USB

	Communication & Monitoring — SNMP
	Optional

	Communication & Monitoring — Display
	LCD

	Environment — Operating temperature
	0–40°C

	Environment — Relative humidity
	20–90% RH (non-condensing)

	Environment — Noise level
	<50dBA @1m

	External battery configuration — Charging current
	1 / 2 / 4 / 6A (adjustable)

	External battery configuration — Battery quantity
	16–20 (adjustable)

	External battery configuration — Product dimensions
	400×438×88mm

	External battery configuration — Net weight
	17kg
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