UPS UNINTERRUPTIBLE POWER SUPPLY

# Lithium Rack-Mounted Online UPS 1KVA-3KVA Series

Exact model: NX-UP-RM-002

PRODUCT IMAGES

| NX-UP-RM-002 · Primary | NX-UP-RM-002 · Gallery |
| --- | --- |

PRODUCT OVERVIEW

19-inch rack-mountable online UPS with built-in LiFePO4 lithium battery. Lighter weight and longer cycle life for space-constrained server cabinets.

| Product line | UPS Uninterruptible Power Supply |
| --- | --- |
| Series / family | Standalone model |
| Exact model | NX-UP-RM-002 |
| Applications | Server racks and cabinets, Network infrastructure, Data centers, Telecommunications, Limited space installations |

MODEL IDENTIFICATION

| Exact model | Product / variant | Topology | Power Range | Phase |
| --- | --- | --- | --- | --- |
| NX-UP-RM-002 | Lithium Rack-Mounted Online UPS 1KVA-3KVA Series | Online Double Conversion | 1KVA-3KVA / 900W-2700W | Single phase input / Single phase output |

TECHNICAL SPECIFICATIONS

| Parameter | Specification |
| --- | --- |
| Topology | Online Double Conversion |
| Power Range | 1KVA-3KVA / 900W-2700W |
| Phase | Single phase input / Single phase output |
| Form Factor | 19-inch Rack Mount |
| Waveform | Pure sine wave |
| Power Factor | 0.9 |
| Battery Types | LiFePO4 (Lithium Iron Phosphate) |
| SKU | NX-UP-RM-002 |
| Available Configurations | SP1KR(S); SP2KR(S); SP3KR(S) |
| Exact Configuration | Confirm one listed configuration during RFQ review |
| Destination Requirements | To be confirmed |

ENGINEERING TABLES

NX-UP-RM-002 · Complete Model Specifications — SP1KR(S) | SP2KR(S) | SP3KR(S)

| Parameter | SP1KR(S) | SP2KR(S) | SP3KR(S) |
| --- | --- | --- | --- |
| Rated capacity | 1KVA / 900W | 2KVA / 1800W | 3KVA / 2700W |
| Battery configuration | Built-in LiFePO4 | Built-in LiFePO4 | Built-in LiFePO4 |
| Dimensions | Not provided | Not provided | Not provided |
| Net weight | Not provided | Not provided | Not provided |
| Transfer time | 0ms | 0ms | 0ms |
| Efficiency | AC: 94.5%; Battery: 87.5% | AC: 95.5%; Battery: 89.5% | AC: 95.5%; Battery: 91.5% |
| Model configuration — Rated capacity | 1KVA / 900W | 2KVA / 1800W | 3KVA / 2700W |
| Model configuration — Battery configuration | Built-in LiFePO4 | Built-in LiFePO4 | Built-in LiFePO4 |
| Model configuration — Transfer time | 0ms | 0ms | 0ms |
| Model configuration — Efficiency | AC: 94.5%; Battery: 87.5% | AC: 95.5%; Battery: 89.5% | AC: 95.5%; Battery: 91.5% |
| Input — Input voltage | 100/110/115/120/127VAC or 200/208/220/230/240VAC | 100/110/115/120/127VAC or 200/208/220/230/240VAC | 100/110/115/120/127VAC or 200/208/220/230/240VAC |
| Input — Input voltage range | 110–300VAC | 110–300VAC | 110–300VAC |
| Input — Derating range | 110–176VAC / 280–300VAC | 110–176VAC / 280–300VAC | 110–176VAC / 280–300VAC |
| Input — Input frequency | 44–56Hz / 54–66Hz | 44–56Hz / 54–66Hz | 44–56Hz / 54–66Hz |
| Input — Input power factor | ≥0.999 | ≥0.999 | ≥0.999 |
| Input — Wiring | L+N+PE | L+N+PE | L+N+PE |
| Output — Output voltage | 100/110/115/120/127VAC or 200/208/220/230/240VAC | 100/110/115/120/127VAC or 200/208/220/230/240VAC | 100/110/115/120/127VAC or 200/208/220/230/240VAC |
| Output — Voltage regulation | ±1% | ±1% | ±1% |
| Output — Synchronized frequency | 44–56Hz / 54–66Hz | 44–56Hz / 54–66Hz | 44–56Hz / 54–66Hz |
| Output — Output power factor | 0.9 / 1.0 | 0.9 / 1.0 | 0.9 / 1.0 |
| Output — THD (linear load) | ≤3% | ≤3% | ≤3% |
| Output — THD (non-linear load) | ≤6% | ≤6% | ≤6% |
| Overload — AC-mode overload | 102–110%: 30min; 110–130%: 10min; 130–150%: 30s; >150%: 200ms | 102–110%: 30min; 110–130%: 10min; 130–150%: 30s; >150%: 200ms | 102–110%: 30min; 110–130%: 10min; 130–150%: 30s; >150%: 200ms |
| Overload — Battery-mode overload | 102–110%: 1min; 110–130%: 10s; 130–150%: 3s; >150%: 200ms | 102–110%: 1min; 110–130%: 10s; 130–150%: 3s; >150%: 200ms | 102–110%: 1min; 110–130%: 10s; 130–150%: 3s; >150%: 200ms |
| Charging — Charging current | 1–8A (adjustable) | 1–8A (adjustable) | 1–8A (adjustable) |
| Charging — Optional battery pack | Yes | Yes | Yes |
| Communication & Monitoring — Communication interface | RS232 / USB / AS400 / RS485 / SNMP | RS232 / USB / AS400 / RS485 / SNMP | RS232 / USB / AS400 / RS485 / SNMP |
| Communication & Monitoring — Display | LCD | LCD | LCD |
| Environment — Operating temperature | -25–55°C | -25–55°C | -25–55°C |
| Environment — Relative humidity | 20–95% RH (non-condensing) | 20–95% RH (non-condensing) | 20–95% RH (non-condensing) |
| Environment — Noise level | <50dBA @1m | <50dBA @1m | <50dBA @1m |
| Battery — Battery voltage | 24/36/48VDC | 48VDC | 48VDC |
| Battery — Battery energy | 960Wh | 960Wh | 960Wh |
| Battery — BMS current | >50A | >50A | >60A |
| External battery configuration — Charging current | 1–12A (adjustable) | 1–12A (adjustable) | 1–12A (adjustable) |
| External battery configuration — Battery voltage | 24/36/48VDC | 48/72VDC | 48/72/96VDC |
| External battery configuration — Net weight | 5.6kg | 8.6kg | 8.9kg |