UPS UNINTERRUPTIBLE POWER SUPPLY

# 3-Phase High Frequency UPS 10KVA-200KVA Series

Exact model: NX-UP-3P-001

PRODUCT IMAGES

| NX-UP-3P-001 · Primary | NX-UP-3P-001 · Gallery |
| --- | --- |

PRODUCT OVERVIEW

Three-phase high frequency online UPS with DSP control and N+X parallel redundancy. Seven model variants covering 10KVA to 200KVA for data centers and commercial facilities.

| Product line | UPS Uninterruptible Power Supply |
| --- | --- |
| Series / family | Standalone model |
| Exact model | NX-UP-3P-001 |
| Applications | Data centers, Large server rooms, Financial institutions, Telecommunications hubs, Transportation systems, Power industry |

MODEL IDENTIFICATION

| Exact model | Product / variant | Topology | Power Range | Phase |
| --- | --- | --- | --- | --- |
| NX-UP-3P-001 | 3-Phase High Frequency UPS 10KVA-200KVA Series | Online Double Conversion with DSP | 10KVA-200KVA / 8KW-160KW | 3-phase + N input / 3-phase + N output |

TECHNICAL SPECIFICATIONS

| Parameter | Specification |
| --- | --- |
| Topology | Online Double Conversion with DSP |
| Power Range | 10KVA-200KVA / 8KW-160KW |
| Phase | 3-phase + N input / 3-phase + N output |
| Form Factor | Tower; Floor-standing |
| Waveform | Pure sine wave |
| Power Factor | 0.8 |
| Battery Types | External VRLA battery bank |
| SKU | NX-UP-3P-001 |
| Available Configurations | 3C3 10K(S); 3C3 20K(S); 3C3 30K(S); 3C3 40K(S); 3C3 60K(S); 3C3 80K(S); 3C3 100-200K(S) |
| Exact Configuration | Confirm one listed configuration during RFQ review |
| Destination Requirements | To be confirmed |

ENGINEERING TABLES

NX-UP-3P-001 · Complete Model Specifications — 3C3 10K(S) | 3C3 20K(S) | 3C3 30K(S) | 3C3 40K(S)

| Parameter | 3C3 10K(S) | 3C3 20K(S) | 3C3 30K(S) | 3C3 40K(S) |
| --- | --- | --- | --- | --- |
| Rated capacity | 10KVA / 8KW | 20KVA / 16KW | 30KVA / 24KW | 40KVA / 32KW |
| Battery configuration | External battery bank | External battery bank | External battery bank | External battery bank |
| Dimensions | 592×250×826mm | 592×250×826mm | 815×250×826mm | 815×300×1000mm |
| Net weight | 38kg | 40kg | 64kg | 82kg |
| Transfer time | 0ms | 0ms | 0ms | 0ms |
| Efficiency | AC: 93% / ECO: 96% / Battery: 90% | AC: 93% / ECO: 96% / Battery: 91% | AC: 93% / ECO: 96% / Battery: 91% | AC: 95% / ECO: 98% / Battery: 93% |
| Model configuration — Rated capacity | 10KVA / 8KW | 20KVA / 16KW | 30KVA / 24KW | 40KVA / 32KW |
| Model configuration — Battery configuration | External battery bank | External battery bank | External battery bank | External battery bank |
| Model configuration — Product dimensions | 592×250×826mm | 592×250×826mm | 815×250×826mm | 815×300×1000mm |
| Model configuration — Net weight | 38kg | 40kg | 64kg | 82kg |
| Model configuration — Transfer time | 0ms | 0ms | 0ms | 0ms |
| Model configuration — Efficiency | AC: 93% / ECO: 96% / Battery: 90% | AC: 93% / ECO: 96% / Battery: 91% | AC: 93% / ECO: 96% / Battery: 91% | AC: 95% / ECO: 98% / Battery: 93% |
| Input — Input voltage | 3×400VAC (3ph+N) | 3×400VAC (3ph+N) | 3×400VAC (3ph+N) | 3×400VAC (3ph+N) |
| Input — Input voltage range at 50% load | 190–520VAC | 190–520VAC | 190–520VAC | 190–520VAC |
| Input — Input voltage range at 100% load | 305–520VAC | 305–520VAC | 305–520VAC | 305–520VAC |
| Input — Input frequency | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz |
| Input — Input power factor | ≥0.99 @100% load | ≥0.99 @100% load | ≥0.99 @100% load | ≥0.99 @100% load |
| Output — Output voltage | 3×360/380/400/415VAC (3ph+N) | 3×360/380/400/415VAC (3ph+N) | 3×360/380/400/415VAC (3ph+N) | 3×360/380/400/415VAC (3ph+N) |
| Output — Voltage regulation | ±1% | ±1% | ±1% | ±1% |
| Output — Synchronized frequency | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz |
| Output — Battery-mode frequency | 50/60Hz ±0.1Hz | 50/60Hz ±0.1Hz | 50/60Hz ±0.1Hz | 50/60Hz ±0.1Hz |
| Output — Current crest ratio | 3:1 | 3:1 | 3:1 | 3:1 |
| Output — THD (linear load) | ≤2% | ≤2% | ≤2% | ≤2% |
| Output — THD (non-linear load) | ≤5% | ≤5% | ≤5% | ≤5% |
| Output — Parallel capacity | Up to 3 units | Up to 3 units | Up to 3 units | Up to 3 units |
| Overload — AC-mode overload | 100–110%: 10min; 110–130%: 1min; >130%: 1s | 100–110%: 10min; 110–130%: 1min; >130%: 1s | 100–110%: 10min; 110–130%: 1min; >130%: 1s | 100–110%: 10min; 110–130%: 1min; >130%: 1s |
| Overload — Battery-mode overload | 100–110%: 30s; 110–130%: 10s; >130%: 1s | 100–110%: 30s; 110–130%: 10s; >130%: 1s | 100–110%: 30s; 110–130%: 10s; >130%: 1s | 100–110%: 30s; 110–130%: 10s; >130%: 1s |
| External battery configuration — Battery quantity | 16–20 | 16–20 | 16–20 | 16–20 |
| Communication & Monitoring — Communication interface | RS232 / USB | RS232 / USB | RS232 / USB | RS232 / USB |
| Communication & Monitoring — SNMP | Optional | Optional | Optional | Optional |
| Communication & Monitoring — Display | LCD | LCD | LCD | LCD |
| Environment — Operating temperature | 0–40°C | 0–40°C | 0–40°C | 0–40°C |
| Environment — Relative humidity | 0–95% RH (non-condensing) | 0–95% RH (non-condensing) | 0–95% RH (non-condensing) | 0–95% RH (non-condensing) |
| Environment — Noise level | <60dBA @1m | <60dBA @1m | <60dBA @1m | <60dBA @1m |

NX-UP-3P-001 · Complete Model Specifications — 3C3 60K(S) | 3C3 80K(S) | 3C3 100-200K(S)

| Parameter | 3C3 60K(S) | 3C3 80K(S) | 3C3 100-200K(S) |
| --- | --- | --- | --- |
| Rated capacity | 60KVA / 48KW | 80KVA / 64KW | 100KVA-200KVA / 80KW-160KW |
| Battery configuration | External battery bank | External battery bank | External battery bank |
| Dimensions | 790×360×900mm | 790×360×900mm | Not provided |
| Net weight | 95kg | 150kg | Not provided |
| Transfer time | 0ms | 0ms | 0ms |
| Efficiency | AC: 95% / ECO: 98% / Battery: 93% | AC: 95% / ECO: 98% / Battery: 93% | AC: 95% / ECO: 98% / Battery: 93% |
| Model configuration — Rated capacity | 60KVA / 48KW | 80KVA / 64KW | 100KVA-200KVA / 80KW-160KW |
| Model configuration — Battery configuration | External battery bank | External battery bank | External battery bank |
| Model configuration — Product dimensions | 790×360×900mm | 790×360×900mm | Not provided |
| Model configuration — Net weight | 95kg | 150kg | Not provided |
| Model configuration — Transfer time | 0ms | 0ms | 0ms |
| Model configuration — Efficiency | AC: 95% / ECO: 98% / Battery: 93% | AC: 95% / ECO: 98% / Battery: 93% | AC: 95% / ECO: 98% / Battery: 93% |
| Input — Input voltage | 3×400VAC (3ph+N) | 3×400VAC (3ph+N) | 3×400VAC (3ph+N) |
| Input — Input voltage range at 50% load | 190–520VAC | 190–520VAC | 190–520VAC |
| Input — Input voltage range at 100% load | 305–520VAC | 305–520VAC | 305–520VAC |
| Input — Input frequency | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz |
| Input — Input power factor | ≥0.99 @100% load | ≥0.99 @100% load | ≥0.99 @100% load |
| Output — Output voltage | 3×360/380/400/415VAC (3ph+N) | 3×360/380/400/415VAC (3ph+N) | 3×360/380/400/415VAC (3ph+N) |
| Output — Voltage regulation | ±1% | ±1% | ±1% |
| Output — Synchronized frequency | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz |
| Output — Battery-mode frequency | 50/60Hz ±0.1Hz | 50/60Hz ±0.1Hz | 50/60Hz ±0.1Hz |
| Output — Current crest ratio | 3:1 | 3:1 | 3:1 |
| Output — THD (linear load) | ≤2% | ≤2% | ≤2% |
| Output — THD (non-linear load) | ≤5% | ≤5% | ≤5% |
| Output — Parallel capacity | Up to 3 units | Up to 3 units | Up to 3 units |
| Overload — AC-mode overload | 100–110%: 10min; 110–130%: 1min; >130%: 1s | 100–110%: 10min; 110–130%: 1min; >130%: 1s | 100–110%: 10min; 110–130%: 1min; >130%: 1s |
| Overload — Battery-mode overload | 100–110%: 30s; 110–130%: 10s; >130%: 1s | 100–110%: 30s; 110–130%: 10s; >130%: 1s | 100–110%: 30s; 110–130%: 10s; >130%: 1s |
| External battery configuration — Battery quantity | 16–20 | 16–20 | 16–20 |
| Communication & Monitoring — Communication interface | RS232 / USB | RS232 / USB | RS232 / USB |
| Communication & Monitoring — SNMP | Optional | Optional | Optional |
| Communication & Monitoring — Display | LCD | LCD | LCD |
| Environment — Operating temperature | 0–40°C | 0–40°C | 0–40°C |
| Environment — Relative humidity | 0–95% RH (non-condensing) | 0–95% RH (non-condensing) | 0–95% RH (non-condensing) |
| Environment — Noise level | <60dBA @1m | <60dBA @1m | <60dBA @1m |