UPS UNINTERRUPTIBLE POWER SUPPLY

# High Frequency Online UPS 1KVA-10KVA Series

Exact model: NX-UP-HF-001

PRODUCT IMAGES

| NX-UP-HF-001 · Primary | NX-UP-HF-001 · Gallery |
| --- | --- |

PRODUCT OVERVIEW

True online double conversion UPS series delivering pure sine wave output with zero transfer time. Five models from 1KVA to 10KVA with VRLA battery.

| Product line | UPS Uninterruptible Power Supply |
| --- | --- |
| Series / family | Standalone model |
| Exact model | NX-UP-HF-001 |
| Applications | Network management centers, Banking and securities, Telecommunications, Medical equipment, Industrial control systems, Government and defense data systems |

MODEL IDENTIFICATION

| Exact model | Product / variant | Topology | Power Range | Phase |
| --- | --- | --- | --- | --- |
| NX-UP-HF-001 | High Frequency Online UPS 1KVA-10KVA Series | Online Double Conversion | 1KVA-10KVA / 900W-9000W | Single phase input / Single phase output |

TECHNICAL SPECIFICATIONS

| Parameter | Specification |
| --- | --- |
| Topology | Online Double Conversion |
| Power Range | 1KVA-10KVA / 900W-9000W |
| Phase | Single phase input / Single phase output |
| Form Factor | Tower |
| Waveform | Pure sine wave |
| Power Factor | 0.9 |
| Battery Types | VRLA sealed lead-acid |
| SKU | NX-UP-HF-001 |
| Available Configurations | SP1K; SP2K; SP3K; SP6K; SP10K |
| Exact Configuration | Confirm one listed configuration during RFQ review |
| Destination Requirements | To be confirmed |

ENGINEERING TABLES

NX-UP-HF-001 · Complete Model Specifications — SP1K | SP2K | SP3K | SP6K

| Parameter | SP1K | SP2K | SP3K | SP6K |
| --- | --- | --- | --- | --- |
| Rated capacity | 1KVA / 900W | 2KVA / 1800W | 3KVA / 2700W | 6KVA / 5400W |
| Battery configuration | 12V/7Ah × 2 | 12V/7Ah × 4 | 12V/7Ah × 6 | 12V/7Ah × 16 |
| Dimensions | 280×148×220mm | 395×148×220mm | 425×192×320mm | 500×248×616mm |
| Net weight | 8.1kg | 14.2kg | 20.8kg | 57kg |
| Transfer time | 0ms | 0ms | 0ms | 0ms |
| Efficiency | AC: 93% / Battery: 91% | AC: 93% / Battery: 91% | AC: 95% / Battery: 92% | AC: 93% / Battery: 90% |
| Model configuration — Rated capacity | 1KVA / 900W | 2KVA / 1800W | 3KVA / 2700W | 6KVA / 5400W |
| Model configuration — Battery configuration | 12V/7Ah × 2 | 12V/7Ah × 4 | 12V/7Ah × 6 | 12V/7Ah × 16 |
| Model configuration — Product dimensions | 280×148×220mm | 395×148×220mm | 425×192×320mm | 500×248×616mm |
| Model configuration — Net weight | 8.1kg | 14.2kg | 20.8kg | 57kg |
| Model configuration — Transfer time | 0ms | 0ms | 0ms | 0ms |
| Model configuration — Efficiency | AC: 93% / Battery: 91% | AC: 93% / Battery: 91% | AC: 95% / Battery: 92% | AC: 93% / Battery: 90% |
| Input — Input voltage | 100/110/115/120/127VAC or 200/208/220/230/240VAC | 100/110/115/120/127VAC or 200/208/220/230/240VAC | 100/110/115/120/127VAC or 200/208/220/230/240VAC | 100/110/115/120/127VAC or 200/208/220/230/240VAC |
| Input — Input voltage range | 115–300VAC | 115–300VAC | 115–300VAC | 115–300VAC |
| Input — Input frequency | 40–70Hz | 40–70Hz | 40–70Hz | 40–70Hz |
| Input — Input power factor | ≥0.99 @100% load | ≥0.99 @100% load | ≥0.99 @100% load | ≥0.99 @100% load |
| Output — Output voltage | 100/110/115/120/127VAC or 200/208/220/230/240VAC | 100/110/115/120/127VAC or 200/208/220/230/240VAC | 100/110/115/120/127VAC or 200/208/220/230/240VAC | 100/110/115/120/127VAC or 200/208/220/230/240VAC |
| Output — Voltage regulation | ±1% | ±1% | ±1% | ±1% |
| Output — Synchronized frequency | 47–53Hz / 57–63Hz | 47–53Hz / 57–63Hz | 47–53Hz / 57–63Hz | 47–53Hz / 57–63Hz |
| Output — Battery-mode frequency | 50Hz ±0.25Hz / 60Hz ±0.3Hz | 50Hz ±0.25Hz / 60Hz ±0.3Hz | 50Hz ±0.25Hz / 60Hz ±0.3Hz | 50Hz ±0.25Hz / 60Hz ±0.3Hz |
| Output — Current crest ratio | 3:1 | 3:1 | 3:1 | 3:1 |
| Output — THD (linear load) | ≤3% | ≤3% | ≤3% | ≤3% |
| Output — THD (non-linear load) | ≤6% | ≤6% | ≤6% | ≤6% |
| Charging — Standard battery | 12V/7Ah | 12V/7Ah | 12V/7Ah | 12V/7Ah |
| Charging — Charging time | 6h to 90% capacity | 6h to 90% capacity | 6h to 90% capacity | 6h to 90% capacity |
| Charging — Charging current | 1A | 1A | 1A | 1A |
| Charging — Standard charging voltage | 27.4VDC ±1% | 54.7VDC ±1% | 82.1VDC ±1% | 218.4VDC ±1% |
| Communication & Monitoring — Communication interface | RS232 / USB | RS232 / USB | RS232 / USB | RS232 / USB |
| Communication & Monitoring — SNMP | Optional | Optional | Optional | Optional |
| Communication & Monitoring — Display | LCD | LCD | LCD | LCD |
| Environment — Operating temperature | 0–40°C | 0–40°C | 0–40°C | 0–40°C |
| Environment — Relative humidity | 20–90% RH (non-condensing) | 20–90% RH (non-condensing) | 20–90% RH (non-condensing) | 20–90% RH (non-condensing) |
| Environment — Noise level | <50dBA @1m | <50dBA @1m | <50dBA @1m | <50dBA @1m |
| External battery configuration — Battery quantity | 3 | 6 | 8 | 16–20 (adjustable) |
| External battery configuration — Charging current | 1 / 2 / 4 / 6A (adjustable) | 1 / 2 / 4 / 6A (adjustable) | 1 / 2 / 4 / 6A (adjustable) | 1 / 2 / 4 / 6A (adjustable) |
| External battery configuration — Charging voltage | 41VDC ±1% | 54.7VDC ±1% | 109VDC ±1% | 218.4VDC ±1% |
| External battery configuration — Product dimensions | 280×148×220mm | 460×190×330mm | 425×192×320mm | 500×248×460mm |
| External battery configuration — Net weight | 4.1kg | 6.2kg | 11kg | 18kg |

NX-UP-HF-001 · Complete Model Specifications — SP10K

| Parameter | SP10K |
| --- | --- |
| Rated capacity | 10KVA / 9000W |
| Battery configuration | 12V/7Ah × 16 |
| Dimensions | 500×248×616mm |
| Net weight | 68kg |
| Transfer time | 0ms |
| Efficiency | AC: 94% / Battery: 91% |
| Model configuration — Rated capacity | 10KVA / 9000W |
| Model configuration — Battery configuration | 12V/7Ah × 16 |
| Model configuration — Product dimensions | 500×248×616mm |
| Model configuration — Net weight | 68kg |
| Model configuration — Transfer time | 0ms |
| Model configuration — Efficiency | AC: 94% / Battery: 91% |
| Input — Input voltage | 100/110/115/120/127VAC or 200/208/220/230/240VAC |
| Input — Input voltage range | 115–300VAC |
| Input — Input frequency | 40–70Hz |
| Input — Input power factor | ≥0.99 @100% load |
| Output — Output voltage | 100/110/115/120/127VAC or 200/208/220/230/240VAC |
| Output — Voltage regulation | ±1% |
| Output — Synchronized frequency | 47–53Hz / 57–63Hz |
| Output — Battery-mode frequency | 50Hz ±0.25Hz / 60Hz ±0.3Hz |
| Output — Current crest ratio | 3:1 |
| Output — THD (linear load) | ≤3% |
| Output — THD (non-linear load) | ≤6% |
| Charging — Standard battery | 12V/7Ah |
| Charging — Charging time | 6h to 90% capacity |
| Charging — Charging current | 1A |
| Charging — Standard charging voltage | 273VDC ±1% |
| Communication & Monitoring — Communication interface | RS232 / USB |
| Communication & Monitoring — SNMP | Optional |
| Communication & Monitoring — Display | LCD |
| Environment — Operating temperature | 0–40°C |
| Environment — Relative humidity | 20–90% RH (non-condensing) |
| Environment — Noise level | <50dBA @1m |
| External battery configuration — Battery quantity | 16–20 (adjustable) |
| External battery configuration — Charging current | 1 / 2 / 4 / 6A (adjustable) |
| External battery configuration — Charging voltage | 273VDC ±1% |
| External battery configuration — Product dimensions | 500×248×460mm |
| External battery configuration — Net weight | 20kg |