UPS UNINTERRUPTIBLE POWER SUPPLY

# High Frequency Online UPS 10KVA-30KVA Series

Exact model: NX-UP-HF-003

PRODUCT IMAGES

| NX-UP-HF-003 · Primary | NX-UP-HF-003 · Gallery |
| --- | --- |

PRODUCT OVERVIEW

Mid-power online UPS series with single/three-phase input flexibility. Four models from 10KVA to 30KVA with external battery bank configuration.

| Product line | UPS Uninterruptible Power Supply |
| --- | --- |
| Series / family | Standalone model |
| Exact model | NX-UP-HF-003 |
| Applications | Medium server rooms, Network centers, Banking and financial systems, Telecommunications infrastructure, Medical equipment, Industrial control |

MODEL IDENTIFICATION

| Exact model | Product / variant | Topology | Power Range | Phase |
| --- | --- | --- | --- | --- |
| NX-UP-HF-003 | High Frequency Online UPS 10KVA-30KVA Series | Online Double Conversion | 10KVA–30KVA / 8000W–24000W | Three phase input / Single phase output |

TECHNICAL SPECIFICATIONS

| Parameter | Specification |
| --- | --- |
| Topology | Online Double Conversion |
| Power Range | 10KVA–30KVA / 8000W–24000W |
| Phase | Three phase input / Single phase output |
| Form Factor | Tower |
| Waveform | Pure sine wave |
| Power Factor | 0.8 |
| Battery Types | External VRLA battery bank |
| SKU | NX-UP-HF-003 |
| Available Configurations | 3C10K(S); 3C15K(S); 3C20K(S); 3C30K(S) |
| Exact Configuration | Confirm one listed configuration during RFQ review |
| Destination Requirements | To be confirmed |

ENGINEERING TABLES

NX-UP-HF-003 · Complete Model Specifications — 3C10K(S) | 3C15K(S) | 3C20K(S) | 3C30K(S)

| Parameter | 3C10K(S) | 3C15K(S) | 3C20K(S) | 3C30K(S) |
| --- | --- | --- | --- | --- |
| Rated capacity | 10KVA / 8000W | 15KVA / 12000W | 20KVA / 16000W | 30KVA / 24000W |
| Battery configuration | External battery bank | External battery bank | External battery bank | External battery bank |
| Dimensions | Not provided | Not provided | Not provided | Not provided |
| Net weight | Not provided | Not provided | Not provided | Not provided |
| Transfer time | 0ms | 0ms | 0ms | 0ms |
| Efficiency | AC: 91%; Battery: 91% | AC: 91%; Battery: 91% | AC: 93%; Battery: 92% | AC: 91%; Battery: 90% |
| Model configuration — Rated capacity | 10KVA / 8000W | 15KVA / 12000W | 20KVA / 16000W | 30KVA / 24000W |
| Model configuration — Battery configuration | External battery bank | External battery bank | External battery bank | External battery bank |
| Model configuration — Transfer time | 0ms | 0ms | 0ms | 0ms |
| Model configuration — Efficiency | AC: 91%; Battery: 91% | AC: 91%; Battery: 91% | AC: 93%; Battery: 92% | AC: 91%; Battery: 90% |
| Input — Input voltage | 380/400/415VAC (3ph+N) | 380/400/415VAC (3ph+N) | 380/400/415VAC (3ph+N) | 380/400/415VAC (3ph+N) |
| Input — Input voltage range at 50% load | 190–520VAC | 190–520VAC | 190–520VAC | 190–520VAC |
| Input — Input voltage range at 100% load | 305–520VAC | 305–520VAC | 305–520VAC | 305–520VAC |
| Input — Input frequency | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz |
| Input — Input power factor | ≥0.8 @100% load | ≥0.8 @100% load | ≥0.8 @100% load | ≥0.8 @100% load |
| Output — Output voltage | 208/220/230/240VAC | 208/220/230/240VAC | 208/220/230/240VAC | 208/220/230/240VAC |
| Output — Voltage regulation | ±1% | ±1% | ±1% | ±1% |
| Output — Synchronized frequency | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz |
| Output — Battery-mode frequency | 50/60Hz ±0.2Hz | 50/60Hz ±0.2Hz | 50/60Hz ±0.2Hz | 50/60Hz ±0.2Hz |
| Output — Current crest ratio | 3:1 | 3:1 | 3:1 | 3:1 |
| Output — THD (linear load) | ≤3% | ≤3% | ≤3% | ≤3% |
| Output — THD (non-linear load) | ≤5% | ≤5% | ≤5% | ≤5% |
| External battery configuration — Battery quantity | 16–20 (adjustable) | 16–20 (adjustable) | 16–20 (adjustable) | 16–20 (adjustable) |
| External battery configuration — Charging current | 4A preset; 1 / 2 / 4 / 6A adjustable | 4A preset; 1 / 2 / 4 / 6A adjustable | 4A preset; 1 / 2 / 4 / 6A adjustable | 4A preset; 1 / 2 / 4 / 6A adjustable |
| External battery configuration — Charging voltage | 218.4 / 273VDC ±1% | 218.4 / 273VDC ±1% | 218.4 / 273VDC ±1% | 218.4 / 273VDC ±1% |
| Communication & Monitoring — Communication interface | RS232 / USB | RS232 / USB | RS232 / USB | RS232 / USB |
| Communication & Monitoring — SNMP | Optional | Optional | Optional | Optional |
| Communication & Monitoring — Display | LCD | LCD | LCD | LCD |
| Environment — Operating temperature | 0–45°C | 0–45°C | 0–45°C | 0–45°C |
| Environment — Relative humidity | 20–95% RH (non-condensing) | 20–95% RH (non-condensing) | 20–95% RH (non-condensing) | 20–95% RH (non-condensing) |
| Environment — Noise level | <60dBA @1m | <60dBA @1m | <60dBA @1m | <60dBA @1m |