UPS UNINTERRUPTIBLE POWER SUPPLY

# Rack-Mounted Online UPS 1KVA-10KVA Series

Exact model: NX-UP-RM-001

PRODUCT IMAGES

| NX-UP-RM-001 · Primary | NX-UP-RM-001 · Gallery |
| --- | --- |

PRODUCT OVERVIEW

19-inch rack-mountable online UPS series with true double conversion. Five models from 1KVA to 10KVA for server cabinet and structured cabling integration.

| Product line | UPS Uninterruptible Power Supply |
| --- | --- |
| Series / family | Standalone model |
| Exact model | NX-UP-RM-001 |
| Applications | Server racks and cabinets, Network infrastructure, Data centers, Telecommunications, Industrial control systems |

MODEL IDENTIFICATION

| Exact model | Product / variant | Topology | Power Range | Phase |
| --- | --- | --- | --- | --- |
| NX-UP-RM-001 | Rack-Mounted Online UPS 1KVA-10KVA Series | Online Double Conversion | 1KVA-10KVA / 900W-9000W | Single phase input / Single phase output |

TECHNICAL SPECIFICATIONS

| Parameter | Specification |
| --- | --- |
| Topology | Online Double Conversion |
| Power Range | 1KVA-10KVA / 900W-9000W |
| Phase | Single phase input / Single phase output |
| Form Factor | 19-inch Rack Mount |
| Waveform | Pure sine wave |
| Power Factor | 0.9 (1–3kVA); 0.8 (6–10kVA) |
| Battery Types | VRLA sealed lead-acid; External battery (extended runtime) |
| SKU | NX-UP-RM-001 |
| Available Configurations | C1KR(S); C2KR(S); C3KR(S); C6KR(S); C10KR(S) |
| Exact Configuration | Confirm one listed configuration during RFQ review |
| Destination Requirements | To be confirmed |

ENGINEERING TABLES

NX-UP-RM-001 · Complete Model Specifications — C1KR(S) | C2KR(S) | C3KR(S) | C6KR(S)

| Parameter | C1KR(S) | C2KR(S) | C3KR(S) | C6KR(S) |
| --- | --- | --- | --- | --- |
| Rated capacity | 1KVA / 900W | 2KVA / 1800W | 3KVA / 2700W | 6KVA / 4800W |
| Battery configuration | Internal VRLA | Internal VRLA | Internal VRLA | Internal VRLA + External option |
| Dimensions | Not provided | Not provided | Not provided | Not provided |
| Net weight | Not provided | Not provided | Not provided | Not provided |
| Transfer time | 0ms | 0ms | 0ms | 0ms |
| Efficiency | AC: 92%; Battery: 90% | AC: 92%; Battery: 90% | AC: 92%; Battery: 90% | AC: 92%; Battery: 90% |
| Model configuration — Rated capacity | 1KVA / 900W | 2KVA / 1800W | 3KVA / 2700W | 6KVA / 4800W |
| Model configuration — Battery configuration | Internal VRLA | Internal VRLA | Internal VRLA | Internal VRLA + External option |
| Model configuration — Transfer time | 0ms | 0ms | 0ms | 0ms |
| Model configuration — Efficiency | AC: 92%; Battery: 90% | AC: 92%; Battery: 90% | AC: 92%; Battery: 90% | AC: 92%; Battery: 90% |
| Input — Input voltage | 100/110/115/120/127VAC or 200/208/220/230/240VAC | 100/110/115/120/127VAC or 200/208/220/230/240VAC | 100/110/115/120/127VAC or 200/208/220/230/240VAC | 100/110/115/120/127VAC or 200/208/220/230/240VAC |
| Input — Input frequency | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz |
| Input — Input power factor | ≥0.99 @100% load | ≥0.99 @100% load | ≥0.99 @100% load | ≥0.99 @100% load |
| Input — Input voltage range at 50% load | 55–145VAC / 110–300VAC | 55–145VAC / 110–300VAC | 55–145VAC / 110–300VAC | 110–300VAC ±3% |
| Input — Input voltage range at 100% load | 85–140VAC / 160–280VAC | 85–140VAC / 160–280VAC | 85–140VAC / 160–280VAC | 176–300VAC ±3% |
| Output — Output voltage | 100/110/115/120/127VAC or 200/208/220/230/240VAC | 100/110/115/120/127VAC or 200/208/220/230/240VAC | 100/110/115/120/127VAC or 200/208/220/230/240VAC | 100/110/115/120/127VAC or 200/208/220/230/240VAC |
| Output — Voltage regulation | ±1% | ±1% | ±1% | ±1% |
| Output — Synchronized frequency | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz | 46–54Hz / 56–64Hz |
| Output — Current crest ratio | 3:1 | 3:1 | 3:1 | 3:1 |
| Output — THD (linear load) | ≤3% | ≤3% | ≤3% | ≤3% |
| Output — THD (non-linear load) | ≤6% | ≤6% | ≤6% | ≤6% |
| Output — Battery-mode frequency | 50Hz ±0.25Hz / 60Hz ±0.3Hz | 50Hz ±0.25Hz / 60Hz ±0.3Hz | 50Hz ±0.25Hz / 60Hz ±0.3Hz | 50/60Hz ±0.1Hz |
| Communication & Monitoring — Communication interface | RS232 / USB | RS232 / USB | RS232 / USB | RS232 / USB |
| Communication & Monitoring — SNMP | Optional | Optional | Optional | Optional |
| Communication & Monitoring — Display | LCD | LCD | LCD | LCD |
| Environment — Operating temperature | 0–40°C | 0–40°C | 0–40°C | 0–40°C |
| Environment — Relative humidity | 20–90% RH (non-condensing) | 20–90% RH (non-condensing) | 20–90% RH (non-condensing) | 20–90% RH (non-condensing) |
| Environment — Noise level | <50dBA @1m | <50dBA @1m | <50dBA @1m | <50dBA @1m |
| External battery configuration — Charging current | 1 / 2 / 4 / 6A (adjustable) | 1 / 2 / 4 / 6A (adjustable) | 1 / 2 / 4 / 6A (adjustable) | 1 / 2 / 4 / 6A (adjustable) |
| External battery configuration — Battery quantity | 2 / 3 | 4 | 6 | 16–20 (adjustable) |
| External battery configuration — Product dimensions | 400×438×88mm | 400×438×88mm | 400×438×88mm | 400×438×88mm |
| External battery configuration — Net weight | 5.6kg | 8.6kg | 8.6kg | 13kg |

NX-UP-RM-001 · Complete Model Specifications — C10KR(S)

| Parameter | C10KR(S) |
| --- | --- |
| Rated capacity | 10KVA / 8000W |
| Battery configuration | Internal VRLA + External option |
| Dimensions | Not provided |
| Net weight | Not provided |
| Transfer time | 0ms |
| Efficiency | AC: 93%; Battery: 91% |
| Model configuration — Rated capacity | 10KVA / 8000W |
| Model configuration — Battery configuration | Internal VRLA + External option |
| Model configuration — Transfer time | 0ms |
| Model configuration — Efficiency | AC: 93%; Battery: 91% |
| Input — Input voltage | 100/110/115/120/127VAC or 200/208/220/230/240VAC |
| Input — Input frequency | 46–54Hz / 56–64Hz |
| Input — Input power factor | ≥0.99 @100% load |
| Input — Input voltage range at 50% load | 110–300VAC ±3% |
| Input — Input voltage range at 100% load | 176–300VAC ±3% |
| Output — Output voltage | 100/110/115/120/127VAC or 200/208/220/230/240VAC |
| Output — Voltage regulation | ±1% |
| Output — Synchronized frequency | 46–54Hz / 56–64Hz |
| Output — Current crest ratio | 3:1 |
| Output — THD (linear load) | ≤3% |
| Output — THD (non-linear load) | ≤6% |
| Output — Battery-mode frequency | 50/60Hz ±0.1Hz |
| Communication & Monitoring — Communication interface | RS232 / USB |
| Communication & Monitoring — SNMP | Optional |
| Communication & Monitoring — Display | LCD |
| Environment — Operating temperature | 0–40°C |
| Environment — Relative humidity | 20–90% RH (non-condensing) |
| Environment — Noise level | <50dBA @1m |
| External battery configuration — Charging current | 1 / 2 / 4 / 6A (adjustable) |
| External battery configuration — Battery quantity | 16–20 (adjustable) |
| External battery configuration — Product dimensions | 400×438×88mm |
| External battery configuration — Net weight | 17kg |